|  | - Powered with AC 230V or AC 24V - Temperature and humidity measurement - Temperature or temperature and humidity control - Heating or cooling - On/Off, PWM, On/Off 3-wire or 3-position control of heating / cooling actuators - Automatic or manual fan speed control: 1-speed, 3-speed or DC Fan - Automatic or manual heating / cooling changeover - Multifunctional inputs for keycard contact, external sensor, etc. - Adjustable commissioning and control parameters - Backlit LCD - KNX bus communications |
| --- | --- |

| Plant diagram |  |
| --- | --- |

| Description of general functions | When"2-pipe fan coil unit" is selected (via DIP switches or tool), the following functions are available. For details see basic documentation (A6V11545892 for RDG200KN) |
| --- | --- |

|  | Control sequence |  |  |
| --- | --- | --- | --- |
|  | - Control of thermal or motorized valve actuators (On/Off, On/Off 3-wire, PWM or 3-position) |  |  |
|  | - Heating only or cooling only |  |  |
|  | - Manual or automatic heating / cooling changeover |  | Other functions |
|  |  |  | - Button lock |
|  | Fan control |  | - 2nd line display setting |
|  | - 1-speed, 3-speed or DC fan, automatic |  | - Setting access with password protection |
|  | - Manual speed control on room thermostat |  | - Valve exercising to prevent from gripping |
|  | - Fan control in dead zone |  |  |
|  | - Fan start related to the coil temperature |  | - Humidity control |
|  |  |  | - By shifting temperature setpoint |
|  | Room and humidity temperature measurement |  | - By controlling an external equipment |
|  | - Internal sensor |  |  |
|  | - External room temperature sensor |  | - 3 multifunctional inputs |
|  | - External return air sensor |  | - Temperature (room, return air, changeover …) |
|  |  |  | - Digital (changeover, presence, window contact …) |
| Device list | <START StandardDeviceList> Legend; Type of unit; Data sheet; Product no.; Qty.. N1; Room thermostat with KNX communications, AC 24 V or AC 230 V, for fan coil units and universal applications; A6V11545853; RDG200KN; 1. YHC; 2- or 3-port valve; V..P4..; 1. Actuator for small valves, 2-position, PWM, 3-position, On/Off or DC 0…10 V, AC 24 V or AC 230 V; SS..3.. / ST..2..; 1. <END StandardDeviceList> |
|  | + For selection of actuators and valves please refer to the product catalog |  |  |

| Optional | <START OptionalDeviceList> Legend; Type of unit; Data sheet; Product no.; Qty.. B1; Cable temperature sensor PVC 2.5 m, NTC 3 kOhm, with connectors 2.8 x 0.8 mm; N1840; QAH11; 1. B2; Cable temperature sensor PVC 2.5 m, NTC 3 kOhm, with connectors 2.8 x 0.8 mm; N1840; QAH11; 1. <END OptionalDeviceList> |
| --- | --- |

| Variants | <START VariantsDeviceList> Legend; Type of unit; Data sheet; Product no.; Qty.. B1a; Room temperature sensor NTC 3 kOhm; N1747; QAA32; 1. <END VariantsDeviceList> |
| --- | --- |

| Connection diagram | DC 0…10 V fan; 1-speed/3-speed fan. |
| --- | --- |

|  | N1 | Room thermostat RDG200KN |  | B1, B2, B3 | Optional external sensors |
| --- | --- | --- | --- | --- | --- |
|  | M1 | 1-speed, 3-speed or DC 0…10 V fan |  | S1, S2, S3 | Optional switches |
|  | YHC | Heating / cooling valve actuator (On/Off, On/Off 3-wire, PWM or 3-position) |  | CE+, CE- | KNX bus |
|  | Notes - Type of control output selectable via DIP switches and parameter P201 Y1&Y3 (On/Off, On/Off 3-wire, PWM or 3-position). - Multifunctional input function selectable via parameters P150…P156 (Room temp. / return air temp, H/C changeover, window contact, dewpoint sensor, fault input) - 3-speed, 1-speed or DC fan selectable via parameter P351 +[P356 … P365] - [P400] Q1 – Switch On in H demand - [P401] Q2 – No function - [P402] Q3 – Switch ON in C demand |  |  |  |  |

| Setting option | Device can be set via |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
|  | - DIP switches and parameters - Smartphone APP PCT Go for Android™  [P500] NFC - Remotely via KNX tools such as Siemens ACS or ETS5 |  |  |  |  |
| DIP switch settings | Application | DIP switches |  |  | Remark |
|  | Remote configuration (factory setting) |  |  |  | Application, outputs and parameters will be downloaded via commissioning tool |
|  |  | ON = | OFF = |  |  |
|  |  | DIP No.: 1…8 | DIP No.: 1…8 |  |  |
| Application | 2-pipe fan coil unit |  |  |  | Set DIP switch 1 |
| Control outputs | - Heating / cooling actuator On/Off, PWM or On/Off 3-wires |  |  |  | Set DIP switch 7 If DIP = "2 position (PWM)": Select On/Off, PWM or On/Off 3-wires via P201 - On/Off = 4 (factory setting) - PWM = 3 - On/Off 3-wires = 2 |
|  | - Heating / cooling actuator 3-position |  |  |  |  |
| Fan | - DC fan |  |  |  | Set DIP switch 6 If DIP = "3-speed fan": Select 1-speed fan, 3-speed fan via P351 - 1-speed fan = 1 - 3-speed fan = 2 |
|  | - 1-speed fan, 3-speed fan |  |  |  |  |

| Main settings | Function | Parameters | Remarks |
| --- | --- | --- | --- |
| Control sequence | Select the control sequence(s) of the controller | P001 = 0…3 | 0 = Heating only |
|  |  |  | 1 = Cooling only (Factory setting) |
|  |  |  | 2 = H/C changeover auto |
|  |  |  | 3 = H/C changeover manual |
| General parameters | User operating mode profile | P002 = 1…3 | 1 = Auto – Protection (Factory setting) 2 = Auto – Comfort – Economy – Protection 3 = Auto – Protection Hospitality |
|  | User fan mode selection | P003 = 0...3 | 0 = Auto – Manual (Factory setting) 1 = Manual 2 = Auto – Manual – Protection 3 = Auto – Protection |
|  | Standard temperature display | P008 = 0, 1 | 0 = Room temperature (Factory setting) 1 = Setpoint |
|  | Additional display information | P009 = 0…5 | 0 = --- (No display) (Factory setting) 1 = °C and °F 2 = Outside temperature (via bus) 3 = Time of day (12 h) (via bus) 4 = Time of day (24 h) (via bus) 5 = Humidity |
|  | Comfort setpoint | P011 = 5...40 °C | Factory setting 21 °C |
|  | Economy heating setpoint | P019 = OFF, 5 °C…P020 | Factory setting 15 °C |
|  | Economy cooling setpoint | P020 =OFF, P019…40 °C | Factory setting 30 °C |

| Multifunctional inputs, digital input | External / return air temperature | P150 = 1 | Factory set on X1 (NTC 3k ¦ LG-Ni1000) |
| --- | --- | --- | --- |
|  | No function | P153 = 0 | Factory set on X2 (H/C changeover ¦ …) |
|  | Window contact | P155 = 3 | Factory set on U1 |
| Inputs selection | 0 = --- (no function) |  | 7 = Monitor input (Digital)(DI) |
|  | 1 = Room temp ext. sensor / return (AI) |  | 8 = Monitor input (Temp) (AI) |
|  | 2 = H/C changeover (AI/DI) |  | 9 = Supply air sensor (AI) |
|  | 3 = Window contact [PROT] (DI) |  | 10 = Presence detector / card reader (DI) |
|  | 4 = Dewpoint sensor (DI) |  | 11 = External temperature limit (AI) |
|  | 5 = Enable electric heater (DI) |  | 12 = Coil temperature (AI) |
|  | 6 = Fault input (DI) |  | 13 = Hotel presence detector / card reader (DI) |
| Fan setting | Fan type 1-speed | P351 = 1 |  |
|  | Fan type 3-speed | P351 = 2 |  |
|  | DC fan 0…10V (ECM) | P351 = 3 |  |
| Humidity control | Control strategy | P450 = 0 | Only temperature control (default) |
|  |  | P450 = 1 | Temperature and humidity control |
|  | Humidity setpoint high | P024 = OFF, P026 or 20…90 % | Factory setting: 50 |
|  | Humidity setpoint low | P026 = OFF, 20…90 % or P024 | Factory setting: OFF |
|  | Max. shift temp setpoint (Dehumid.) | P461 = -3...3 K | Temperature setpoint deviation due to the humidity in the room |
| Engineering | For a complete list of parameters and detailed description of functions see basic documentation: A6V11545892 for RDG200KN; PI controller settings [P050 … P064] For engineering of RDG in conjunction with Synco see CE1P3127 (Communication via the KNX bus for Synco 700, Basic documentation) |  |  |

Preselection reception: Com. Obj 	1 bit

Time switch reception: Com. Obj	---

State transmission: Com. Obj		---

Window status input				Local

Presence detector input				Local | Bus

Presence detector function		Standard

| Energy efficiency | Heating control |  | Evaluation | Definition of classes |  |  |  | Remarks |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  | RDG200KN | Non residential |  |  |  |  |
|  |  |  |  | D | C | B | A |  |
|  | Emission control The control system is installed at the emitter or room level, for case 1 one system can control several rooms |  |  |  |  |  |  |  |
|  | 0 | No automatic control |  |  |  |  |  |  |
|  | 1 | Central automatic control |  |  |  |  |  |  |
|  | 2 | Individual room automatic control by thermostatic valves or electronic controller | X |  |  |  |  |  |
|  | 3 | Individual room control with communication between controllers and to BACS |  |  |  |  |  |  |
|  | 4 | Integrated individual room control including demand control (by occupancy, air quality, etc.) | X |  |  |  |  | 29 |
|  | Control of distribution network hot water temperature (supply or return) Similar function can be applied to the control of direct electric heating networks |  |  |  |  |  |  | 7 |
|  | 0 | No automatic control |  |  |  |  |  |  |
|  | 1 | Outside temperature compensated control |  |  |  |  |  |  |
|  | 2 | Indoor temperature control |  |  |  |  |  |  |
|  | Control of distribution pumps The controlled pumps can be installed at different levels in the network |  |  |  |  |  |  | 7 |
|  | 0 | No control |  |  |  |  |  |  |
|  | 1 | On off control |  |  |  |  |  |  |
|  | 2 | Variable speed pump control with constant p |  |  |  |  |  |  |
|  | 3 | Variable speed pump control with proportional p |  |  |  |  |  |  |
|  | Intermittent control of emission and/or distribution One controller can control different rooms/zone having same occupancy patterns |  |  |  |  |  |  | 7 |
|  | 0 | No automatic control |  |  |  |  |  |  |
|  | 1 | Automatic control with fixed time program |  |  |  |  |  |  |
|  | 2 | Automatic control with optimum start/stop |  |  |  |  |  |  |
|  | Generator control |  |  |  |  |  |  | 7 |
|  | 0 | Constant temperature |  |  |  |  |  |  |
|  | 1 | Variable temperature depending on outdoor temperature |  |  |  |  |  |  |
|  | 2 | Variable temperature depending on the load |  |  |  |  |  |  |
|  | Sequencing of different generators |  |  |  |  |  |  | 7 |
|  | 0 | Priorities only based on loads |  |  |  |  |  |  |
|  | 1 | Priorities based on loads and generator capacities |  |  |  |  |  |  |
|  | 2 | Priorities based on generator efficiency (check other standard) |  |  |  |  |  |  |

| Energy efficiency | Cooling control |  | Evaluation | Definition of classes |  |  |  | Remarks |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  | RDG200KN | Non residential |  |  |  |  |
|  |  |  |  | D | C | B | A |  |
|  | Emission control The control system is installed at the emitter or room level, for case 1 one system can control several rooms |  |  |  |  |  |  |  |
|  | 0 | No automatic control |  |  |  |  |  |  |
|  | 1 | Central automatic control |  |  |  |  |  |  |
|  | 2 | Individual room automatic control by thermostatic valves or electronic controller | X |  |  |  |  |  |
|  | 3 | Individual room control with communication between controllers and to BACS |  |  |  |  |  |  |
|  | 4 | Integrated individual room control including demand control (by occupancy, air quality, etc.) | X |  |  |  |  | 29 |
|  | Control of distribution network cold water temperature (supply or return) Similar function can be applied to the control of direct electric heating networks |  |  |  |  |  |  | 7 |
|  | 0 | No automatic control |  |  |  |  |  |  |
|  | 1 | Outside temperature compensated control |  |  |  |  |  |  |
|  | 2 | Indoor temperature control |  |  |  |  |  |  |
|  | Control of distribution pumps The controlled pumps can be installed at different levels in the network |  |  |  |  |  |  | 7 |
|  | 0 | No control |  |  |  |  |  |  |
|  | 1 | On off control |  |  |  |  |  |  |
|  | 2 | Variable speed pump control with constant p |  |  |  |  |  |  |
|  | 3 | Variable speed pump control with proportional p |  |  |  |  |  |  |
|  | Intermittent control of emission and/or distribution One controller can control different rooms/zone having same occupancy patterns |  |  |  |  |  |  | 7 |
|  | 0 | No automatic control |  |  |  |  |  |  |
|  | 1 | Automatic control with fixed time program |  |  |  |  |  |  |
|  | 2 | Automatic control with optimum start/stop |  |  |  |  |  |  |
|  | Interlock between heating and cooling control of emission and/or distribution |  |  |  |  |  |  | 7 |
|  | 0 | No interlock |  |  |  |  |  |  |
|  | 1 | Partial interlock (dependent of the HVAC system) |  |  |  |  |  |  |
|  | 2 | Total interlock |  |  |  |  |  |  |
|  | Generator control |  |  |  |  |  |  | 7 |
|  | 0 | Constant temperature |  |  |  |  |  |  |
|  | 1 | Variable temperature depending on outdoor temperature |  |  |  |  |  |  |
|  | 2 | Variable temperature depending on the load |  |  |  |  |  |  |
|  | Sequencing of different generators |  |  |  |  |  |  | 7 |
|  | 0 | Priorities only based on loads |  |  |  |  |  |  |
|  | 1 | Priorities based on loads and generator capacities |  |  |  |  |  |  |
|  | 2 | Priorities based on generator efficiency (check other standard) |  |  |  |  |  |  |
| Summary | Energy efficiency class: RDG200KN A |  |  |  |  |  |  |  |

| Remarks | No. | Remark |
| --- | --- | --- |
|  | 7 | Only together with Efficiency Class A application |
|  | 29 | Presence detector required |
|  | Home automation / building automation and control system and technical home/building management required satisfying Efficiency Class A |  |
|  | Efficiency Class rating based on EN15232:2007 |  |

| Issued by Siemens Switzerland Ltd Smart Infrastructure Global Headquarters Theilerstrasse 1a CH-6300 Zug Tel. +41 58 724 2424 www.siemens.com/buildingtechnologies | © Siemens Switzerland Ltd, 2020 Technical specifications and availability subject to change without notice. |
| --- | --- |