## INFO
This spreadsheet is distributed to the Commission services as part of the deliverables of the study "Support for setting up a Smart Readiness Indicator for buildings and related impact assessment".
It contains following tabs:
* Overview_of_services | This is list with all smart ready services and their functionality levels. Column L indicates whether the services are part of the proposed streamlined set
* tabs for the various domains: heating, dhw, cooling, etc. | These tabs provide further details on the various services, including the provisional impact scores for each of the service levels
version: june 2020

## overview_of_services
Domain | Code | Service group | Smart ready service | Functionality level 0 (as non-smart default) | Functionality level 1 | Functionality level 2 | Functionality level 3 | Functionality level 4 | Standard used | Actionable | part of the proposed detailed method | Preconditions / Dependency on other services or building types
Heating | Heating-1a | Heat control - demand side | Heat emission control | No automatic control | Central automatic control (e.g. central thermostat) | Individual room control (e.g. thermostatic valves, or electronic controller) | Individual room control with communication between controllers and to BACS | Individual room control with communication and occupancy detection | EN 15232 | 1 | 1 | Always to be assessed
Heating | Heating-1b | Heat control - demand side | Emission control for TABS (heating mode) | No automatic control | Central automatic control | Advanced central automatic control | Advanced central automatic control with intermittent operation and/or room temperature feedback control |  | EN 15232 | 1 | 1 | Triage: only relevant in case of TABS. Mostly restricted to non-residential buildings
Heating | Heating-1c | Heat control - demand side | Control of distribution fluid temperature (supply or return air flow or water flow) - Similar function can be applied to the control of direct electric heating networks | No automatic control | Outside temperature compensated control | Demand based control |  |  | EN 15232 | 1 | 1 | Not applicable in case of individual heaters (e.g. stoves)
Heating | Heating-1d | Heat control - demand side | Control of distribution pumps in networks | No automatic control | On off control | Multi-Stage control | Variable speed pump control (pump unit (internal) estimations) | Variable speed pump control (external demand signal) | EN 15232 | 1 | 1 | Only applicable for hydronic heating systems
Heating | Heating-1f | Heat control - demand side | Thermal Energy Storage (TES) for building heating (excluding TABS) | Continuous storage operation | Time-scheduled storage operation | Load prediction based storage operation | Heat storage capable of flexible control through grid signals (e.g. DSM) |  |  | 1 | 1 | Only applicable in case thermal energy storage is present.
Heating | Heating-2a | Control heat production facilities | Heat generator control (all except heat pumps) | Constant temperature control | Variable temperature control depending on outdoor temperature | Variable temperature control depending on the load (e.g. depending on supply water temperature set point) |  |  | EN 15232 | 1 | 1 | Only applicable in case of combustion heater or district heating
Heating | Heating-2b | Control heat production facilities | Heat generator control (for heat pumps) | On/Off-control of heat generator | Multi-stage control of heat generator capacity depending on the load or demand (e.g. on/off of several compressors) | Variable control of heat generator capacity depending on the load or demand (e.g. hot gas bypass, inverter frequency control) | Variable control of heat generator capacity depending on the load AND external signals from grid |  | EN 15232 + expanded | 1 | 1 | Only applicable in case of heat pumps
Heating | Heating-2d | Control heat production facilities | Sequencing in case of different heat generators | Priorities only based on running time | Control according to fixed priority list: e.g. based on rated energy efficiency | Control according to dynamic priority list (based on current energy efficiency, carbon emissions and capacity of generators, e.g. solar, geothermal heat, cogeneration plant, fossil fuels) | Control according to dynamic priority list (based on current AND predicted load, energy efficiency, carbon emissions and capacity of generators) | Control according to dynamic priority list (based on current AND predicted load, energy efficiency, carbon emissions, capacity of generators AND external signals from grid) | EN 15232 + expanded | 1 | 1 | Only applicable in case of multiple heat generators, mostly restricted to large buildings
Heating | Heating-3 | Information to occupants and facility managers | Report information regarding HEATING system performance | None | Central or remote reporting of current performance KPIs (e.g. temperatures, submetering energy usage) | Central or remote reporting of current performance KPIs and historical data | Central or remote reporting of performance evaluation including forecasting and/or benchmarking | Central or remote reporting of performance evaluation including forecasting and/or benchmarking; also including predictive management and fault detection | No standards available | 1 | 1
Heating | Heating-4 | Flexibility and grid interaction | Flexibility and grid interaction | No automatic control | Scheduled operation of heating system | Self-learning optimal control of heating system | Heating system capable of flexible control through grid signals (e.g. DSM) | Optimized control of heating system based on local predictions and grid signals (e.g. through model predictive control) | None | ? | 1 | The inspectability of the nature of the control algorithm would need to be facilitated
Domestic hot water | DHW-1a | Control DHW production facilities | Control of DHW storage charging (with direct electric heating or integrated electric heat pump) | Automatic control on / off | Automatic control on / off and scheduled charging enable | Automatic control on / off and scheduled charging enable and multi-sensor storage management | Automatic charging control based on local availability of renewables or information from electricity grid (DR, DSM) |  | EN 15232, except level 3 | 1 | 1 | Only applicable in case of DHW storage with electric heating
Domestic hot water | DHW-1b | Control DHW production facilities | Control of DHW storage charging (using hot water generation) | Automatic control on / off | Automatic control on / off and scheduled charging enable | Automatic on/off control, scheduled charging enable and demand-based supply temperature control or multi-sensor storage management | DHW production system capable of automatic charging control based on external signals (e.g. from district heating grid) |  | EN 15232, except level 3 | 1 | 1 | Only applicable in case of DHW storage with non-electrical heat generation
Domestic hot water | DHW-1d | Control DHW production facilities | Control of DHW storage charging (with solar collector and supplymentary heat generation) | Manual selected control of solar energy or heat generation | Automatic control of solar storage charge (Prio. 1) and supplementary storage charge | Automatic control of solar storage charge (Prio. 1) and supplementary storage charge and demand-oriented supply or multi-sensor storage management | Automatic control of solar storage charge (Prio. 1) and supplementary storage charge, demand-oriented supply and return temperature control and multi-sensor storage management |  | EN 15232 | 1 | 1 | Only applicable in case of DHW storage with solar collector
Domestic hot water | DHW-2b | Control DHW production facilities | Sequencing in case of different DHW generators | Priorities only based on running time | Control according to fixed priority list: e.g. based on rated energy efficiency | Control according to dynamic priority list (based on current energy efficiency, carbon emissions and capacity of generators, e.g. solar, geothermal heat, cogeneration plant, fossil fuels) | Control according to dynamic priority list (based on current AND predicted load, energy efficiency, carbon emissions and capacity of generators) | Control according to dynamic priority list (based on current AND predicted load, energy efficiency, carbon emissions, capacity of generators AND external signals from grid) |  | 1 | 1
Domestic hot water | DHW-3 | Information to occupants and facility managers | Report information regarding domestic hot water performance | None | Indication of actual values (e.g. temperatures, submetering energy usage) | Actual values and historical data | Performance evaluation including forecasting and/or benchmarking | Performance evaluation including forecasting and/or benchmarking; also including predictive management and fault detection | No standards available | 1 | 1
Cooling | Cooling-1a | Cooling control - demand side | Cooling emission control | No automatic control | Central automatic control | Individual room control | Individual room control with communication between controllers and to BACS | Individual room control with communication and occupancy detection | EN 15232 | 1 | 1 | Only applicable in case mechanical cooling systems are present
Cooling | Cooling-1b | Cooling control - demand side | Emission control for TABS (cooling mode) | No automatic control | Central automatic control | Advanced central automatic control | Advanced central automatic control with intermittent operation and/or room temperature feedback control |  | EN 15232 | 1 | 1 | Only applicable in case mechanical cooling systems based on TABS are present
Cooling | Cooling-1c | Cooling control - demand side | Control of distribution network chilled water temperature (supply or return) | Constant temperature control | Outside temperature compensated control | Demand based control |  |  | EN 15232 | 1 | 1 | Only applicable in case mechanical cooling systems with hydronic distribution system are present
Cooling | Cooling-1d | Cooling control - demand side | Control of distribution pumps in networks | No automatic control | On off control | Multi-Stage control | Variable speed pump control (pump unit (internal) estimations) | Variable speed pump control (external demand signal) | EN 15232 | 1 | 1 | Only applicable in case mechanical cooling systems with hydronic distribution system are present
Cooling | Cooling-1f | Cooling control - demand side | Interlock: avoiding simultaneous heating and cooling in the same room | No interlock | Partial interlock (minimising risk of simultanieus heating and cooling e.g. by sliding setpoints) | Total interlock (control system ensures no simultaneous heating and cooling can take place) |  |  | EN 15232 | 1 | 1 | Only applicable in case mechanical cooling systems are present
Cooling | Cooling-1g | Cooling control - demand side | Control of Thermal Energy Storage (TES) operation | Continuous storage operation | Time-scheduled storage operation | Load prediction based storage operation | Cold storage capable of flexible control through grid signals (e.g. DSM) |  | EN 15232 | 1 | 1 | Only applicable in case mechanical cooling systems are present ánd include TES systems
Cooling | Cooling-2a | Control cooling production facilities | Generator control for cooling | On/Off-control of cooling production | Multi-stage control of cooling production capacity depending on the load or demand (e.g. on/off of several compressors) | Variable control of cooling production capacity depending on the load or demand (e.g. hot gas bypass, inverter frequency control) | Variable control of cooling production capacity depending on the load AND external signals from grid |  | EN 15232 | 1 | 1 | Only applicable in case mechanical cooling systems are present
Cooling | Cooling-2b | Control cooling production facilities | Sequencing of different cooling generators | Priorities only based on running times | Fixed sequencing based on loads only: e.g. depending on the generators characteristics such as absorption chiller vs. centrifugal chiller | Dynamic priorities based on generator efficiency and characteristics (e.g. availability of free cooling) | Load prediction based sequencing: the sequence is based on e.g. COP and available power of a device and the predicted required power | Sequencing based on dynamic priority list, including external signals from grid | EN 15232 | 1 | 1 | Only applicable in case multiple mechanical cooling systems are present
Cooling | Cooling-3 | Information to occupants and facility managers | Report information regarding cooling system performance | None | Central or remote reporting of current performance KPIs (e.g. temperatures, submetering energy usage) | Central or remote reporting of current performance KPIs and historical data | Central or remote reporting of performance evaluation including forecasting and/or benchmarking | Central or remote reporting of performance evaluation including forecasting and/or benchmarking; also including predictive management and fault detection | No standards available | 1 | 1 | Only applicable in case mechanical cooling systems are present
Cooling | Cooling-4 | Flexibility and grid interaction | Flexibility and grid interaction | No automatic control | Scheduled operation of cooling system | Self-learning optimal control of cooling system | Cooling system capable of flexible control through grid signals (e.g. DSM) | Optimized control of cooling system based on local predictions and grid signals (e.g. through model predictive control) | None | ? | 1 | The inspectability of the nature of the control algorithm would need to be facilitated
Controlled ventilation | Ventilation-1a | Air flow control | Supply air flow control at the room level | No ventilation system or manual control | Clock control | Occupancy detection control | Central Demand Control based on air quality sensors (CO2, VOC, humidity, ...) | Local Demand Control based on air quality sensors (CO2, VOC,...) with local flow from/to the zone regulated by dampers | EN 15232 + expanded | 1 | 1 | Always to be assessed
Controlled ventilation | Ventilation-1c | Air flow control | Air flow or pressure control at the air handler level | No automatic control: Continuously supplies of air flow for a maximum load of all rooms | On off time control: Continuously supplies of air flow for a maximum load of all rooms during nominal occupancy time | Multi-stage control: To reduce the auxiliary energy demand of the fan | Automatic flow or pressure control without pressure reset: Load dependent supplies of air flow for the demand of all connected rooms. | Automatic flow or pressure control with pressure reset: Load dependent supplies of air flow for the demand of all connected rooms (for variable air volume systems with VFD). | EN 15232 | 1 | 1 | Only in case of mechanical ventilation
Controlled ventilation | Ventilation-2c | Air temperature control | Heat recovery control: prevention of overheating | Without overheating control | Modulate or bypass heat recovery based on sensors in air exhaust | Modulate or bypass heat recovery based on multiple room temperature sensors or predictive control |  |  | EN 15232 + expanded | 1 | 1 | Only in case of mechanical ventilation with heat recovery
Controlled ventilation | Ventilation-2d | Air temperature control | Supply air temperature control at the air handling unit level | No automatic control | Constant setpoint: A control loop enables to control the supply air temperature, the setpoint is constant and can only be modified by a manual action | Variable set point with outdoor temperature compensation | Variable set point with load dependant compensation. A control loop enables to control the supply air temperature. The setpoint is defined as a function of the loads in the room |  | EN 15232 | 1 | 1 | Only in case of mechanical ventilation which supplies heating
Controlled ventilation | Ventilation-3 | Free cooling | Free cooling with mechanical ventilation system | No automatic control | Night cooling | Free cooling: air flows modulated during all periods of time to minimize the amount of mechanical cooling | H,x- directed control: The amount of outside air and recirculation air are modulated during all periods of time to minimize the amount of mechanical cooling. Calculation is performed on the basis of temperatures and humidity (enthalpy). |  | EN 15232 | 1 | 1 | Only in case of mechanical or hybrid ventilation
Controlled ventilation | Ventilation-6 | Feedback - Reporting information | Reporting information regarding IAQ | None | Air quality sensors (e.g. CO2) and real time autonomous monitoring | Real time monitoring & historical information of IAQ available to occupants | Real time monitoring & historical information of IAQ available to occupants + warning on maintenance needs or occupant actions (e.g. window opening) |  | / | ? | 1 | Always to be assessed
Lighting | Lighting-1a | Artificial lighting control | Occupancy control for indoor lighting | Manual on/off switch | Manual on/off switch + additional sweeping extinction signal | Automatic detection (auto on / dimmed or auto off) | Automatic detection (manual on / dimmed or auto off) |  | EN 15232 | 1 | 1 | Always to be assessed
Lighting | Lighting-2 | Control artificial lighting power based on daylight levels | Control artificial lighting power based on daylight levels | Manual (central) | Manual (per room / zone) | Automatic switching | Automatic dimming | Automatic dimming including scene-based light control (during time intervals, dynamic and adapted lighting scenes are set, for example, in terms of illuminance level, different correlated colour temperature (CCT) and the possibility to change the light distribution within the space according to e. g. design, human needs, visual tasks) | EN 15232 + expanded | 1 | 1 | Always to be assessed
Dynamic building envelope | DE-1 | Window control | Window solar shading control | No sun shading or only manual operation | Motorized operation with manual control | Motorized operation with automatic control based on sensor data | Combined light/blind/HVAC control | Predictive blind control (e.g. based on weather forecast) | EN 15232 | 1 | 1 | Only applicable in case movable shades, screens or blinds are present
Dynamic building envelope | DE-2 | Window control | Window open/closed control, combined with HVAC system | Manual operation or only fixed windows | Open/closed detection to shut down heating or cooling systems | Level 1 + Automised mechanical window opening based on room sensor data | Level 2 + Centralized coordination of operable windows, e.g. to control free natural night cooling |  | / | ? | 1
Dynamic building envelope | DE-4 | Feedback - Reporting information | Reporting information regarding performance of dynamic building envelope systems | No reporting | Position of each product & fault detection | Position of each product, fault detection & predictive maintenance | Position of each product, fault detection, predictive maintenance, real-time sensor data (wind, lux, temperature…) | Position of each product, fault detection, predictive maintenance, real-time & historical sensor data (wind, lux, temperature…) | / | 1 | 1 | Only applicable in case movable shades, screens or blinds are present
Electricity | electricity-2 | Feedback - Reporting information | Reporting information regarding local electricity generation | None | Current generation data available | Actual values and historical data | Performance evaluation including forecasting and/or benchmarking | Performance evaluation including forecasting and/or benchmarking; also including predictive management and fault detection | No standards available | ? | 1 | Only applicable in case of local energy generation
| electricity-3 | DER - Storage | Storage of (locally generated) electricity | None | On site storage of electricity (e.g. electric battery) | On site storage of energy (e.g. electric battery or thermal storage) with controller based on grid signals | On site storage of energy (e.g. electric battery or thermal storage) with controller optimising the use of locally generated electricity | On site storage of energy (e.g. electric battery or thermal storage) with controller optimising the use of locally generated electricity and possibility to feed back into the grid | / | ? | 1 | Only applicable in case of local energy generation
Electricity | electricity-4 | DER- Optimization | Optimizing self-consumption of locally generated electricity | None | Scheduling electricity consumption (plug loads, white goods, etc.) | Automated management of local electricity consumption based on current renewable energy availability | Automated management of local electricity consumption based on current and predicted energy needs and renewable energy availability |  | / | ? | 1 | Only applicable in case of local energy generation
Electricity | electricity-5 | DER - Generation Control | Control of combined heat and power plant (CHP) | CHP control based on scheduled runtime management and/or current heat energy demand | CHP runtime control influenced by the fluctuating availability of RES; overproduction will be fed into the grid | CHP runtime control influenced by the fluctuating availability of RES and grid signals; dynamic charging and runtime control to optimise self-consumption of renewables |  |  |  | ? | 1 | Only applicable in case of CHP
Electricity | electricity-8 | DSM- Storage | Support of (micro)grid operation modes | None | Automated management of (building-level) electricity consumption based on grid signals | Automated management of (building-level) electricity consumption and electricity supply to neighbouring buildings (microgrid) or grid | Automated management of (building-level) electricity consumption and supply, with potential to continue limited off-grid operation (island mode) |  |  | 0 | 1
Electricity | electricity-11 | Feedback - Reporting information | Reporting information regarding energy storage | None | Current state of charge (SOC) data available | Actual values and historical data | Performance evaluation including forecasting and/or benchmarking | Performance evaluation including forecasting and/or benchmarking; also including predictive management and fault detection |  | ? | 1 | Only applicable in case of local energy storage
Electricity | Electricity-12 | Feedback - Reporting information | Reporting information regarding electricity consumption | None | reporting on current electricity consumption on building level | real-time feedback or benchmarking on building level | real-time feedback or benchmarking on appliance level | real-time feedback or benchmarking on appliance level with automated personalized recommendations |  | ? | 1
Electric vehicle charging | EV-15 | EV Charging | EV Charging Capacity | not present | ducting (or simple power plug) available | 0-9% of parking spaces has recharging points | 10-50% or parking spaces has recharging point | >50% of parking spaces has recharging point | No standards available | ? | 1 | Only to be assessed if parking spots available on site
Electric vehicle charging | EV-16 | EV Charging - Grid | EV Charging Grid balancing | Not present (uncontrolled charging) | 1-way controlled charging (e.g. including desired departure time and grid signals for optimization) | 2-way controlled charging (e.g. including desired departure time and grid signals for optimization) |  |  | No standards available | ? | 1 | Only to be assessed if EV charging available on site
Electric vehicle charging | EV-17 | EV Charging - connectivity | EV charging information and connectivity | No information available | Reporting information on EV charging status to occupant | Reporting information on EV charging status to occupant AND automatic identification and authorizition of the driver to the charging station (ISO 15118 compliant) |  |  |  | 0 | 1 | Only to be assessed if EV charging available on site
Monitoring and control | MC-3 | HVAC interaction control | Run time management of HVAC systems | Manual setting | Runtime setting of heating and cooling plants following a predefined time schedule | Heating and cooling plant on/off control based on building loads | Heating and cooling plant on/off control based on predictive control or grid signals |  | EN 15232 + expanded with level 3 | ? | 1
Monitoring and control | MC-4 | Fault detection | Detecting faults of technical building systems and providing support to the diagnosis of these faults | No central indication of detected faults and alarms | With central indication of detected faults and alarms for at least 2 relevant TBS | With central indication of detected faults and alarms for all relevant TBS | With central indication of detected faults and alarms for all relevant TBS, including diagnosing functions |  | EN 15232 | 1 | 1
Monitoring and control | MC-9 | TBS interaction control | Occupancy detection: connected services | None | Occupancy detection for individual functions, e.g. lighting | Centralised occupant detection which feeds in to several TBS such as lighting and heating |  |  | / | 0 | 1
Monitoring and control | MC-13 | Feedback - Reporting information | Central reporting of TBS performance and energy use | None | Central or remote reporting of realtime energy use per energy carrier | Central or remote reporting of realtime energy use per energy carrier, combining TBS of at least 2 domains in one interface | Central or remote reporting of realtime energy use per energy carrier, combining TBS of all main domains in one interface |  | / | ? | 1
Monitoring and control | MC-25 | Smart Grid Integration | Smart Grid Integration | None - No harmonization between grid and TBS; building is operated independently from the grid load | Demand side management possible for (some) individual TBS, but not coordinated over various domains | Coordinated demand side management of multiple TBS |  |  | EN15232 | ? | 1 | The inspectability of the nature of the control algorithm would need to be facilitated for level 2. Service 7.5 in EN15232-1-17. Average impacts derived from multiple simulations to produce BACS factors in EN15232.
Monitoring and control | MC-28 | Feedback - Reporting information | Reporting information regarding demand side management performance and operation | None | Reporting information on current DSM status, including managed energy flows | Reporting information on currenthistorical and predicted DSM status, including managed energy flows |  |  | No standards available | ? | 1
Monitoring and control | MC-29 | Override control | Override of DSM control | No DSM control | DSM control without the possibility to override this control by the building user (occupant or facility manager) | Manual override and reactivation of DSM control by the building user | Scheduled override of DSM control (and reactivation) by the building user | Scheduled override of DSM control and reactivation with optimised control | No standards available | ? | 1
Monitoring and control | MC-30 | Single platform that allows automated control & coordination between TBS + optimization of energy flow based on occupancy, weather and grid signals | Single platform that allows automated control & coordination between TBS + optimization of energy flow based on occupancy, weather and grid signals | None | Single platform that allows manual control of multiple TBS | Single platform that allows automated control & coordination between TBS | Single platform that allows automated control & coordination between TBS + optimization of energy flow based on occupancy, weather and grid signals |  | ? | ? | 1 | Always to be assessed

## heating
| domain | heating
| code | service | 1
► | Heating-1a | Heat emission control |  | Service group: | Heat control - demand side
| Functionality levels |  | IMPACTS
|  |  | Energy savings on site | Flexibility for the grid and storage | Comfort | Convenience | Health & wellbeing | maintenance & fault prediction | information to occupants
| level 0 | No automatic control | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 1 | Central automatic control (e.g. central thermostat) | 1 | 0 | 1 | 1 | 1 | 0 | 0
| level 2 | Individual room control (e.g. thermostatic valves, or electronic controller) | 2 | 0 | 2 | 2 | 2 | 0 | 0
| level 3 | Individual room control with communication between controllers and to BACS | 2 | 0 | 2 | 3 | 2 | 1 | 0
| level 4 | Individual room control with communication and occupancy detection | 3 | 0 | 2 | 3 | 2 | 1 | 0
Information sources
|  | Standard? | EN 15232
| code | service | 1
► | Heating-1b | Emission control for TABS (heating mode) |  | Service group: | Heat control - demand side
| Functionality levels |  | IMPACTS
|  |  | Energy savings on site | Flexibility for the grid and storage | Comfort | Convenience | Health & wellbeing | maintenance & fault prediction | information to occupants
| level 0 | No automatic control | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 1 | Central automatic control | 1 | 0 | 1 | 1 | 1 | 0 | 0
| level 2 | Advanced central automatic control | 1 | 0 | 1 | 2 | 2 | 0 | 0
| level 3 | Advanced central automatic control with intermittent operation and/or room temperature feedback control | 2 | 0 | 2 | 3 | 2 | 1 | 1
| level 4 | 0
Information sources
|  | Standard? | EN 15232
| code | service | 1
► | Heating-1c | Control of distribution fluid temperature (supply or return air flow or water flow) - Similar function can be applied to the control of direct electric heating networks |  | Service group: | Heat control - demand side
| Functionality levels |  | IMPACTS
|  |  | Energy savings on site | Flexibility for the grid and storage | Comfort | Convenience | Health & wellbeing | maintenance & fault prediction | information to occupants
| level 0 | No automatic control | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 1 | Outside temperature compensated control | 1 | 0 | 1 | 1 | 0 | 0 | 0
| level 2 | Demand based control | 2 | 0 | 1 | 1 | 0 | 0 | 0
| level 3 | 0 | - | - | - | - | - | - | -
| level 4 | 0
Information sources
|  | Standard? | EN 15232
| code | service | 1
► | Heating-1d | Control of distribution pumps in networks |  | Service group: | Heat control - demand side
| Functionality levels |  | IMPACTS
|  |  | Energy savings on site | Flexibility for the grid and storage | Comfort | Convenience | Health & wellbeing | maintenance & fault prediction | information to occupants
| level 0 | No automatic control | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 1 | On off control | 1 | 0 | 0 | 0 | 0 | 0 | 0
| level 2 | Multi-Stage control | 2 | 0 | 0 | 0 | 0 | 0 | 0
| level 3 | Variable speed pump control (pump unit (internal) estimations) | 2 | 0 | 0 | 0 | 0 | 0 | 0
| level 4 | Variable speed pump control (external demand signal) | 2 | 0 | 0 | 0 | 0 | 0 | 0
Information sources
|  | Standard? | EN 15232
| code | service | 1
► | Heating-1f | Thermal Energy Storage (TES) for building heating (excluding TABS) |  | Service group: | Heat control - demand side
| Functionality levels |  | IMPACTS
|  |  | Energy savings on site | Flexibility for the grid and storage | Comfort | Convenience | Health & wellbeing | maintenance & fault prediction | information to occupants
| level 0 | Continuous storage operation | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 1 | Time-scheduled storage operation | 1 | 0 | 0 | 0 | 0 | 0 | 0
| level 2 | Load prediction based storage operation | 2 | 1 | 0 | 0 | 0 | 0 | 0
| level 3 | Heat storage capable of flexible control through grid signals (e.g. DSM) | 2 | 2 | 0 | 0 | 0 | 0 | 0
| level 4 | 0
Information sources
|  | Standard? | EN 15232
| Functionality levels |  | IMPACTS
|  |  | Energy savings on site | Flexibility for the grid and storage | Comfort | Convenience | Health & wellbeing | maintenance & fault prediction | information to occupants
| level 0 | #REF! | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 1 | #REF! | + | 0 | + | + | 0 | 0 | +
| level 2 | #REF! | ++ | 0 | ++ | ++ | 0 | 0 | +
| level 3 | #REF! | - | - | - | - | - | - | -
| level 4 | #REF!
Information sources
|  | Standard? | EN 15232
| code | service | 1
► | Heating-2a | Heat generator control (all except heat pumps) |  | Service group: | Control heat production facilities
| Functionality levels |  | IMPACTS
|  |  | Energy savings on site | Flexibility for the grid and storage | Comfort | Convenience | Health & wellbeing | maintenance & fault prediction | information to occupants
| level 0 | Constant temperature control | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 1 | Variable temperature control depending on outdoor temperature | 1 | 0 | 1 | 0 | 0 | 0 | 0
| level 2 | Variable temperature control depending on the load (e.g. depending on supply water temperature set point) | 2 | 0 | 2 | 0 | 0 | 0 | 0
| level 3 | 0 | - | - | - | - | - | - | -
| level 4 | 0
Information sources
|  | Standard? | EN 15232
| code | service | 1
► | Heating-2b | Heat generator control (for heat pumps) |  | Service group: | Control heat production facilities
| Functionality levels |  | IMPACTS
|  |  | Energy savings on site | Flexibility for the grid and storage | Comfort | Convenience | Health & wellbeing | maintenance & fault prediction | information to occupants
| level 0 | On/Off-control of heat generator | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 1 | Multi-stage control of heat generator capacity depending on the load or demand (e.g. on/off of several compressors) | 1 | 1 | 1 | 0 | 0 | 0 | 0
| level 2 | Variable control of heat generator capacity depending on the load or demand (e.g. hot gas bypass, inverter frequency control) | 2 | 1 | 2 | 0 | 0 | 0 | 0
| level 3 | Variable control of heat generator capacity depending on the load AND external signals from grid | 2 | 3 | 2 | 0 | 0 | 0 | 0
| level 4 | 0
Information sources
Standard?
| code | service | 1
► | Heating-2d | Sequencing in case of different heat generators |  | Service group: | Control heat production facilities
| Functionality levels |  | IMPACTS
|  |  | Energy savings on site | Flexibility for the grid and storage | Comfort | Convenience | Health & wellbeing | maintenance & fault prediction | information to occupants
| level 0 | Priorities only based on running time | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 1 | Control according to fixed priority list: e.g. based on rated energy efficiency | 1 | 0 | 0 | 0 | 0 | 0 | 0
| level 2 | Control according to dynamic priority list (based on current energy efficiency, carbon emissions and capacity of generators, e.g. solar, geothermal heat, cogeneration plant, fossil fuels) | 2 | 1 | 0 | 0 | 0 | 0 | 0
| level 3 | Control according to dynamic priority list (based on current AND predicted load, energy efficiency, carbon emissions and capacity of generators) | 3 | 2 | 0 | 0 | 0 | 0 | 0
| level 4 | Control according to dynamic priority list (based on current AND predicted load, energy efficiency, carbon emissions, capacity of generators AND external signals from grid) | 3 | 3 | 0 | 0 | 0 | 0 | 0
Information sources
|  | Standard? | EN 15232
| Functionality levels |  | IMPACTS
|  |  | Energy savings on site | Flexibility for the grid and storage | Comfort | Convenience | Wellbeing and health | maintenance & fault prediction | information to occupants
| level 0 | #REF! | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 1 | #REF! | + | 0 | 0 | 0 | 0 | 0 | 0
| level 2 | #REF! | ++ | 0 | 0 | 0 | 0 | 0 | 0
| level 3 | #REF! | +++ | ++ | 0 | 0 | 0 | 0 | 0
| level 4 | #REF!
Information sources
|  | Standard? | EN 15232
| code | service | 1
► | Heating-3 | Report information regarding HEATING system performance |  | Service group: | Information to occupants and facility managers
| Functionality levels |  | IMPACTS
|  |  | Energy savings on site | Flexibility for the grid and storage | Comfort | Convenience | Health & wellbeing | maintenance & fault prediction | information to occupants
| level 0 | None | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 1 | Central or remote reporting of current performance KPIs (e.g. temperatures, submetering energy usage) | 1 | 0 | 0 | 0 | 0 | 1 | 1
| level 2 | Central or remote reporting of current performance KPIs and historical data | 1 | 0 | 0 | 0 | 0 | 1 | 2
| level 3 | Central or remote reporting of performance evaluation including forecasting and/or benchmarking | 1 | 0 | 0 | 0 | 0 | 1 | 3
| level 4 | Central or remote reporting of performance evaluation including forecasting and/or benchmarking; also including predictive management and fault detection | 1 | 0 | 0 | 1 | 0 | 3 | 3
Information sources
Standard?
| code | service | 1
| Heating-4 | Flexibility and grid interaction |  | Service group: | Flexibility and grid interaction
| Functionality levels |  | IMPACTS
|  |  | Energy savings on site | Flexibility for the grid and storage | Comfort | Convenience | Health & wellbeing | maintenance & fault prediction | information to occupants
| level 0 | No automatic control | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 1 | Scheduled operation of heating system | 1 | 0 | 1 | 1 | 0 | 0 | 0
| level 2 | Self-learning optimal control of heating system | 2 | 1 | 2 | 2 | 0 | 0 | 0
| level 3 | Heating system capable of flexible control through grid signals (e.g. DSM) | 2 | 3 | 2 | 3 | 0 | 0 | 0
| level 4 | Optimized control of heating system based on local predictions and grid signals (e.g. through model predictive control) | 2 | 3 | 3 | 3 | 1 | 0 | 0
Information sources
Standard?

## dhw
| domain | domestic hot water
| code | service | 1
► | DHW-1a | Control of DHW storage charging (with direct electric heating or integrated electric heat pump) |  | Service group: | Control DHW production facilities
| Functionality levels |  | IMPACTS
|  |  | Energy savings on site | Flexibility for the grid and storage | Comfort | Convenience | Wellbeing and health | maintenance & fault prediction | information to occupants
| level 0 | Automatic control on / off | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 1 | Automatic control on / off and scheduled charging enable | 1 | 1 | 0 | 1 | 0 | 0 | 0
| level 2 | Automatic control on / off and scheduled charging enable and multi-sensor storage management | 2 | 2 | 0 | 2 | 0 | 0 | 0
| level 3 | Automatic charging control based on local availability of renewables or information from electricity grid (DR, DSM) | 2 | 3 | 0 | 2 | 0 | 0 | 0
| level 4 | 0
Information sources
|  | Standard? | EN 15232
| code | service | 1
► | DHW-1b | Control of DHW storage charging (using hot water generation) |  | Service group: | Control DHW production facilities
| Functionality levels |  | IMPACTS
|  |  | Energy savings on site | Flexibility for the grid and storage | Comfort | Convenience | Wellbeing and health | maintenance & fault prediction | information to occupants
| level 0 | Automatic control on / off | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 1 | Automatic control on / off and scheduled charging enable | 1 | 1 | 0 | 1 | 0 | 0 | 0
| level 2 | Automatic on/off control, scheduled charging enable and demand-based supply temperature control or multi-sensor storage management | 2 | 2 | 0 | 2 | 0 | 0 | 0
| level 3 | DHW production system capable of automatic charging control based on external signals (e.g. from district heating grid) | 2 | 3 | 0 | 2 | 0 | 0 | 0
| level 4 | 0
Information sources
|  | Standard? | EN 15232
| Functionality levels |  | IMPACTS
|  |  | Energy savings on site | Flexibility for the grid and storage | Comfort | Convenience | Wellbeing and health | maintenance & fault prediction | information to occupants
| level 0 | #REF! | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 1 | #REF! | + | + | 0 | + | 0 | 0 | 0
| level 2 | #REF! | ++ | ++ | 0 | ++ | 0 | 0 | 0
| level 3 | #REF! | +++ | +++ | 0 | ++ | 0 | 0 | 0
| level 4 | #REF!
Information sources
|  | Standard? | EN 15232
| code | service | 1
► | DHW-1d | Control of DHW storage charging (with solar collector and supplymentary heat generation) |  | Service group: | Control DHW production facilities
| Functionality levels |  | IMPACTS
|  |  | Energy savings on site | Flexibility for the grid and storage | Comfort | Convenience | Wellbeing and health | maintenance & fault prediction | information to occupants
| level 0 | Manual selected control of solar energy or heat generation | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 1 | Automatic control of solar storage charge (Prio. 1) and supplementary storage charge | 1 | 0 | 0 | 1 | 0 | 0 | 0
| level 2 | Automatic control of solar storage charge (Prio. 1) and supplementary storage charge and demand-oriented supply or multi-sensor storage management | 2 | 1 | 0 | 2 | 0 | 0 | 0
| level 3 | Automatic control of solar storage charge (Prio. 1) and supplementary storage charge, demand-oriented supply and return temperature control and multi-sensor storage management | 3 | 2 | 0 | 2 | 0 | 0 | 0
| level 4 | 0
Information sources
|  | Standard? | EN 15232
| code | service | 1
| DHW-2b | Sequencing in case of different DHW generators |  | Service group: | Control DHW production facilities
| Functionality levels |  | IMPACTS
|  |  | Energy savings on site | Flexibility for the grid and storage | Comfort | Convenience | Wellbeing and health | maintenance & fault prediction | information to occupants
| level 0 | Priorities only based on running time | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 1 | Control according to fixed priority list: e.g. based on rated energy efficiency | 1 | 0 | 0 | 0 | 0 | 0 | 0
| level 2 | Control according to dynamic priority list (based on current energy efficiency, carbon emissions and capacity of generators, e.g. solar, geothermal heat, cogeneration plant, fossil fuels) | 2 | 1 | 0 | 0 | 0 | 0 | 0
| level 3 | Control according to dynamic priority list (based on current AND predicted load, energy efficiency, carbon emissions and capacity of generators) | 3 | 2 | 0 | 0 | 0 | 0 | 0
| level 4 | Control according to dynamic priority list (based on current AND predicted load, energy efficiency, carbon emissions, capacity of generators AND external signals from grid) | 3 | 3 | 0 | 0 | 0 | 0 | 0
Information sources
Standard?
| code | service | 1
► | DHW-3 | Report information regarding domestic hot water performance |  | Service group: | Information to occupants and facility managers
| Functionality levels |  | IMPACTS
|  |  | Energy savings on site | Flexibility for the grid and storage | Comfort | Convenience | Wellbeing and health | maintenance & fault prediction | information to occupants
| level 0 | None | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 1 | Indication of actual values (e.g. temperatures, submetering energy usage) | 1 | 0 | 0 | 0 | 0 | 1 | 1
| level 2 | Actual values and historical data | 1 | 0 | 0 | 0 | 0 | 1 | 2
| level 3 | Performance evaluation including forecasting and/or benchmarking | 1 | 0 | 0 | 0 | 0 | 1 | 3
| level 4 | Performance evaluation including forecasting and/or benchmarking; also including predictive management and fault detection | 1 | 0 | 0 | 1 | 0 | 2 | 3
Information sources
Standard?
| Functionality levels |  | IMPACTS
|  |  | Energy savings on site | Flexibility for the grid and storage | Comfort | Convenience | Wellbeing and health | maintenance & fault prediction | information to occupants
| level 0 | #REF! | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 1 | #REF! | 0 | ++ | 0 | 0 | 0 | 0 | 0
| level 2 | #REF!
| level 3 | #REF!
| level 4 | #REF!
Information sources
Standard?

## cooling
| domain | cooling
| code | service | 1
► | Cooling-1a | Cooling emission control |  | Service group: | Cooling control - demand side
| Functionality levels |  | IMPACTS
|  |  | Energy savings on site | Flexibility for the grid and storage | Comfort | Convenience | Wellbeing and health | maintenance & fault prediction | information to occupants
| level 0 | No automatic control | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 1 | Central automatic control | 1 | 0 | 1 | 1 | 1 | 0 | 0
| level 2 | Individual room control | 1 | 0 | 1 | 2 | 2 | 0 | 0
| level 3 | Individual room control with communication between controllers and to BACS | 2 | 0 | 2 | 3 | 2 | 1 | 0
| level 4 | Individual room control with communication and occupancy detection | 3 | 0 | 2 | 3 | 2 | 1 | 0
Information sources
|  | Standard? | EN 15232
| code | service | 1
► | Cooling-1b | Emission control for TABS (cooling mode) |  | Service group: | Cooling control - demand side
| Functionality levels |  | IMPACTS
|  |  | Energy savings on site | Flexibility for the grid and storage | Comfort | Convenience | Wellbeing and health | maintenance & fault prediction | information to occupants
| level 0 | No automatic control | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 1 | Central automatic control | 1 | 0 | 1 | 1 | 1 | 0 | 0
| level 2 | Advanced central automatic control | 1 | 0 | 1 | 1 | 2 | 0 | 0
| level 3 | Advanced central automatic control with intermittent operation and/or room temperature feedback control | 2 | 0 | 2 | 3 | 2 | 1 | 1
| level 4 | 0
Information sources
|  | Standard? | EN 15232
| code | service | 1
► | Cooling-1c | Control of distribution network chilled water temperature (supply or return) |  | Service group: | Cooling control - demand side
| Functionality levels |  | IMPACTS
|  |  | Energy savings on site | Flexibility for the grid and storage | Comfort | Convenience | Wellbeing and health | maintenance & fault prediction | information to occupants
| level 0 | Constant temperature control | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 1 | Outside temperature compensated control | 1 | 0 | 1 | 1 | 0 | 0 | 0
| level 2 | Demand based control | 2 | 0 | 1 | 1 | 0 | 0 | 0
| level 3 | 0 | - | - | - | - | - | - | -
| level 4 | 0
Information sources
|  | Standard? | EN 15232
| code | service | 1
► | Cooling-1d | Control of distribution pumps in networks |  | Service group: | Cooling control - demand side
| Functionality levels |  | IMPACTS
|  |  | Energy savings on site | Flexibility for the grid and storage | Comfort | Convenience | Wellbeing and health | maintenance & fault prediction | information to occupants
| level 0 | No automatic control | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 1 | On off control | 1 | 0 | 0 | 0 | 0 | 0 | 0
| level 2 | Multi-Stage control | 2 | 0 | 0 | 0 | 0 | 0 | 0
| level 3 | Variable speed pump control (pump unit (internal) estimations) | 2 | 0 | 0 | 0 | 0 | 0 | 0
| level 4 | Variable speed pump control (external demand signal) | 2 | 0 | 0 | 0 | 0 | 0 | 0
Information sources
|  | Standard? | EN 15232
| Functionality levels |  | IMPACTS
|  |  | Energy savings on site | Flexibility for the grid and storage | Comfort | Convenience | Wellbeing and health | maintenance & fault prediction | information to occupants
| level 0 | #REF! | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 1 | #REF! | + | 0 | + | + | 0 | 0 | 0
| level 2 | #REF! | ++ | 0 | + | + | 0 | 0 | 0
| level 3 | #REF! | +++ | 0 | + | + | 0 | 0 | 0
| level 4 | #REF!
Information sources
|  | Standard? | EN 15232
| code | service | 1
► | Cooling-1f | Interlock: avoiding simultaneous heating and cooling in the same room |  | Service group: | Cooling control - demand side
| Functionality levels |  | IMPACTS
|  |  | Energy savings on site | Flexibility for the grid and storage | Comfort | Convenience | Wellbeing and health | maintenance & fault prediction | information to occupants
| level 0 | No interlock | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 1 | Partial interlock (minimising risk of simultanieus heating and cooling e.g. by sliding setpoints) | 2 | 0 | 0 | 0 | 0 | 0 | 0
| level 2 | Total interlock (control system ensures no simultaneous heating and cooling can take place) | 3 | 0 | 0 | 0 | 0 | 0 | 0
| level 3 | 0 | - | - | - | - | - | - | -
| level 4 | 0
Information sources
|  | Standard? | EN 15232
| code | service | 1
► | Cooling-1g | Control of Thermal Energy Storage (TES) operation |  | Service group: | Cooling control - demand side
| Functionality levels |  | IMPACTS
|  |  | Energy savings on site | Flexibility for the grid and storage | Comfort | Convenience | Wellbeing and health | maintenance & fault prediction | information to occupants
| level 0 | Continuous storage operation | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 1 | Time-scheduled storage operation | 1 | 0 | 0 | 0 | 0 | 0 | 0
| level 2 | Load prediction based storage operation | 2 | 1 | 0 | 0 | 0 | 0 | 0
| level 3 | Cold storage capable of flexible control through grid signals (e.g. DSM) | 2 | 2 | 0 | 0 | 0 | 0 | 0
| level 4 | 0
Information sources
|  | Standard? | EN 15232
| code | service | 1
► | Cooling-2a | Generator control for cooling |  | Service group: | Control cooling production facilities
| Functionality levels |  | IMPACTS
|  |  | Energy savings on site | Flexibility for the grid and storage | Comfort | Convenience | Wellbeing and health | maintenance & fault prediction | information to occupants
| level 0 | On/Off-control of cooling production | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 1 | Multi-stage control of cooling production capacity depending on the load or demand (e.g. on/off of several compressors) | 1 | 1 | 1 | 0 | 0 | 0 | 0
| level 2 | Variable control of cooling production capacity depending on the load or demand (e.g. hot gas bypass, inverter frequency control) | 2 | 1 | 2 | 0 | 0 | 0 | 0
| level 3 | Variable control of cooling production capacity depending on the load AND external signals from grid | 2 | 3 | 2 | 0 | 0 | 0 | 0
| level 4 | 0
Information sources
|  | Standard? | EN 15232
| code | service | 1
► | Cooling-2b | Sequencing of different cooling generators |  | Service group: | Control cooling production facilities
| Functionality levels |  | IMPACTS
|  |  | Energy savings on site | Flexibility for the grid and storage | Comfort | Convenience | Wellbeing and health | maintenance & fault prediction | information to occupants
| level 0 | Priorities only based on running times | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 1 | Fixed sequencing based on loads only: e.g. depending on the generators characteristics such as absorption chiller vs. centrifugal chiller | 1 | 0 | 0 | 0 | 0 | 0 | 0
| level 2 | Dynamic priorities based on generator efficiency and characteristics (e.g. availability of free cooling) | 2 | 1 | 0 | 0 | 0 | 0 | 0
| level 3 | Load prediction based sequencing: the sequence is based on e.g. COP and available power of a device and the predicted required power | 3 | 2 | 0 | 0 | 0 | 0 | 0
| level 4 | Sequencing based on dynamic priority list, including external signals from grid | 3 | 3 | 0 | 0 | 0 | 0 | 0
Information sources
|  | Standard? | EN 15232
| code | service | 1
► | Cooling-3 | Report information regarding cooling system performance |  | Service group: | Information to occupants and facility managers
| Functionality levels |  | IMPACTS
|  |  | Energy savings on site | Flexibility for the grid and storage | Comfort | Convenience | Wellbeing and health | maintenance & fault prediction | information to occupants
| level 0 | None | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 1 | Central or remote reporting of current performance KPIs (e.g. temperatures, submetering energy usage) | 1 | 0 | 0 | 0 | 0 | 1 | 1
| level 2 | Central or remote reporting of current performance KPIs and historical data | 1 | 0 | 0 | 0 | 0 | 1 | 2
| level 3 | Central or remote reporting of performance evaluation including forecasting and/or benchmarking | 1 | 0 | 0 | 0 | 0 | 1 | 3
| level 4 | Central or remote reporting of performance evaluation including forecasting and/or benchmarking; also including predictive management and fault detection | 1 | 0 | 0 | 1 | 0 | 3 | 3
Information sources
Standard?
| code | service | 1
| Cooling-4 | Flexibility and grid interaction |  | Service group: | Flexibility and grid interaction
| Functionality levels |  | IMPACTS
|  |  | Energy savings on site | Flexibility for the grid and storage | Comfort | Convenience | Wellbeing and health | maintenance & fault prediction | information to occupants
| level 0 | No automatic control | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 1 | Scheduled operation of cooling system | 1 | 0 | 1 | 1 | 0 | 0 | 0
| level 2 | Self-learning optimal control of cooling system | 2 | 1 | 2 | 2 | 0 | 0 | 0
| level 3 | Cooling system capable of flexible control through grid signals (e.g. DSM) | 2 | 3 | 2 | 3 | 0 | 0 | 0
| level 4 | Optimized control of cooling system based on local predictions and grid signals (e.g. through model predictive control) | 2 | 3 | 3 | 3 | 1 | 0 | 0
Information sources
Standard?

## ventilation
| domain | mechanical ventilation
| code | service | 1
► | Ventilation-1a | Supply air flow control at the room level |  | Service group: | Air flow control
| Functionality levels |  | IMPACTS
|  |  | Energy savings on site | Flexibility for the grid and storage | Comfort | Convenience | Wellbeing and health | maintenance & fault prediction | information to occupants
| level 0 | No ventilation system or manual control | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 1 | Clock control | 1 | 0 | 1 | 1 | 1 | 0 | 0
| level 2 | Occupancy detection control | 1 | 0 | 2 | 2 | 2 | 0 | 0
| level 3 | Central Demand Control based on air quality sensors (CO2, VOC, humidity, ...) | 2 | 0 | 3 | 3 | 3 | 0 | 0
| level 4 | Local Demand Control based on air quality sensors (CO2, VOC,...) with local flow from/to the zone regulated by dampers | 3 | 0 | 3 | 3 | 3 | 0 | 0
Information sources
|  | Standard? | EN 15232
| Functionality levels |  | IMPACTS
|  |  | Energy savings on site | Flexibility for the grid and storage | Comfort | Convenience | Wellbeing and health | maintenance & fault prediction | information to occupants
| level 0 | #REF! | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 1 | #REF! | + | 0 | + | + | + | 0 | 0
| level 2 | #REF! | + | 0 | ++ | ++ | ++ | 0 | 0
| level 3 | #REF! | ++ | 0 | ++ | ++ | ++ | 0 | 0
| level 4 | #REF!
Information sources
|  | Standard? | EN 15232
| code | service | 1
► | Ventilation-1c | Air flow or pressure control at the air handler level |  | Service group: | Air flow control
| Functionality levels |  | IMPACTS
|  |  | Energy savings on site | Flexibility for the grid and storage | Comfort | Convenience | Wellbeing and health | maintenance & fault prediction | information to occupants
| level 0 | No automatic control: Continuously supplies of air flow for a maximum load of all rooms | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 1 | On off time control: Continuously supplies of air flow for a maximum load of all rooms during nominal occupancy time | 1 | 0 | 0 | 0 | 0 | 0 | 0
| level 2 | Multi-stage control: To reduce the auxiliary energy demand of the fan | 2 | 0 | 0 | 0 | 0 | 0 | 0
| level 3 | Automatic flow or pressure control without pressure reset: Load dependent supplies of air flow for the demand of all connected rooms. | 3 | 0 | 0 | 0 | 0 | 0 | 0
| level 4 | Automatic flow or pressure control with pressure reset: Load dependent supplies of air flow for the demand of all connected rooms (for variable air volume systems with VFD). | 3 | 0 | 0 | 0 | 0 | 0 | 0
Information sources
|  | Standard? | EN 15232
| Functionality levels |  | IMPACTS
|  |  | Energy savings on site | Flexibility for the grid and storage | Comfort | Convenience | Wellbeing and health | maintenance & fault prediction | information to occupants
| level 0 | #REF! | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 1 | #REF! | + | 0 | + | + | + | 0 | 0
| level 2 | #REF! | - | - | - | - | - | - | -
| level 3 | #REF! | - | - | - | - | - | - | -
| level 4 | #REF!
Information sources
|  | Standard? | EN 15232
| code | service | 1
► | Ventilation-2c | Heat recovery control: prevention of overheating |  | Service group: | Air temperature control
| Functionality levels |  | IMPACTS
|  |  | Energy savings on site | Flexibility for the grid and storage | Comfort | Convenience | Wellbeing and health | maintenance & fault prediction | information to occupants
| level 0 | Without overheating control | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 1 | Modulate or bypass heat recovery based on sensors in air exhaust | 1 | 0 | 1 | 1 | 1 | 0 | 0
| level 2 | Modulate or bypass heat recovery based on multiple room temperature sensors or predictive control | 2 | 0 | 2 | 2 | 2 | 0 | 0
| level 3 | 0 | - | - | - | - | - | - | -
| level 4 | 0
Information sources
|  | Standard? | EN 15232
| code | service | 1
► | Ventilation-2d | Supply air temperature control at the air handling unit level |  | Service group: | Air temperature control
| Functionality levels |  | IMPACTS
|  |  | Energy savings on site | Flexibility for the grid and storage | Comfort | Convenience | Wellbeing and health | maintenance & fault prediction | information to occupants
| level 0 | No automatic control | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 1 | Constant setpoint: A control loop enables to control the supply air temperature, the setpoint is constant and can only be modified by a manual action | 1 | 0 | 1 | 1 | 0 | 0 | 0
| level 2 | Variable set point with outdoor temperature compensation | 2 | 0 | 2 | 1 | 0 | 0 | 0
| level 3 | Variable set point with load dependant compensation. A control loop enables to control the supply air temperature. The setpoint is defined as a function of the loads in the room | 3 | 0 | 2 | 1 | 0 | 0 | 0
| level 4 | 0
Information sources
|  | Standard? | EN 15232
| code | service | 1
► | Ventilation-3 | Free cooling with mechanical ventilation system |  | Service group: | Free cooling
| Functionality levels |  | IMPACTS
|  |  | Energy savings on site | Flexibility for the grid and storage | Comfort | Convenience | Wellbeing and health | maintenance & fault prediction | information to occupants
| level 0 | No automatic control | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 1 | Night cooling | 1 | 0 | 3 | 2 | 1 | 0 | 0
| level 2 | Free cooling: air flows modulated during all periods of time to minimize the amount of mechanical cooling | 2 | 0 | 3 | 2 | 1 | 0 | 0
| level 3 | H,x- directed control: The amount of outside air and recirculation air are modulated during all periods of time to minimize the amount of mechanical cooling. Calculation is performed on the basis of temperatures and humidity (enthalpy). | 3 | 0 | 3 | 2 | 1 | 0 | 0
| level 4 | 0
Information sources
|  | Standard? | EN 15232
| Functionality levels |  | IMPACTS
|  |  | Energy savings on site | Flexibility for the grid and storage | Comfort | Convenience | Wellbeing and health | maintenance & fault prediction | information to occupants
| level 0 | #REF! | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 1 | #REF! | 0 | 0 | ++ | + | + | 0 | 0
| level 2 | #REF! | 0 | 0 | ++ | + | + | 0 | 0
| level 3 | #REF! | +++ | 0 | ++ | ++ | + | 0 | 0
| level 4 | #REF!
Information sources
Standard?
| code | service | 1
► | Ventilation-6 | Reporting information regarding IAQ |  | Service group: | Feedback - Reporting information
| Functionality levels |  | IMPACTS
|  |  | Energy savings on site | Flexibility for the grid and storage | Comfort | Convenience | Wellbeing and health | maintenance & fault prediction | information to occupants
| level 0 | None | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 1 | Air quality sensors (e.g. CO2) and real time autonomous monitoring | 0 | 0 | 0 | 0 | 2 | 1 | 1
| level 2 | Real time monitoring & historical information of IAQ available to occupants | 0 | 0 | 0 | 0 | 3 | 1 | 2
| level 3 | Real time monitoring & historical information of IAQ available to occupants + warning on maintenance needs or occupant actions (e.g. window opening) | 0 | 0 | 0 | 0 | 3 | 2 | 3
| level 4 | 0
Information sources
Standard?

## lighting
| domain | lighting
| code | service | 1
► | Lighting-1a | Occupancy control for indoor lighting |  | Service group: | Artificial lighting control
| Functionality levels |  | IMPACTS
|  |  | Energy savings on site | Flexibility for the grid and storage | Comfort | Convenience | Wellbeing and health | maintenance & fault prediction | information to occupants
| level 0 | Manual on/off switch | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 1 | Manual on/off switch + additional sweeping extinction signal | 1 | 0 | 1 | 1 | 0 | 0 | 0
| level 2 | Automatic detection (auto on / dimmed or auto off) | 2 | 0 | 2 | 2 | 0 | 0 | 0
| level 3 | Automatic detection (manual on / dimmed or auto off) | 3 | 0 | 2 | 2 | 0 | 0 | 0
| level 4 | 0
Information sources
|  | Standard? | EN 15232
| Functionality levels |  | IMPACTS
|  |  | Energy savings on site | Flexibility for the grid and storage | Comfort | Convenience | Wellbeing and health | maintenance & fault prediction | information to occupants
| level 0 | #REF! | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 1 | #REF! | + | 0 | 0 | + | 0 | 0 | 0
| level 2 | #REF! | + | 0 | 0 | ++ | 0 | 0 | 0
| level 3 | #REF! | + | 0 | +++ | +++ | ++++ | 0 | +
| level 4 | #REF!
Information sources
|  | Standard? | EN 15193-1 and CEN-TR 16791 | CEN-TR 16791 | EN 12464-1 | CEN-TR 16791 | CEN-TR 16791 | CEN-TR 16791 | CEN-TR 16791
| code | service | 1
► | Lighting-2 | Control artificial lighting power based on daylight levels |  | Service group: | Control artificial lighting power based on daylight levels
| Functionality levels |  | IMPACTS
|  |  | Energy savings on site | Flexibility for the grid and storage | Comfort | Convenience | Wellbeing and health | maintenance & fault prediction | information to occupants
| level 0 | Manual (central) | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 1 | Manual (per room / zone) | 1 | 0 | 1 | 1 | 0 | 0 | 0
| level 2 | Automatic switching | 2 | 0 | 1 | 1 | 1 | 0 | 0
| level 3 | Automatic dimming | 3 | 0 | 2 | 2 | 2 | 0 | 0
| level 4 | Automatic dimming including scene-based light control (during time intervals, dynamic and adapted lighting scenes are set, for example, in terms of illuminance level, different correlated colour temperature (CCT) and the possibility to change the light distribution within the space according to e. g. design, human needs, visual tasks) | 3 | 0 | 3 | 3 | 3 | 0 | 0
Information sources
|  | Standard? | EN 15193-1 and CEN-TR 16791 | CEN-TR 16791 | EN 12464-1 | CEN-TR 16791 | CEN-TR 16791 | CEN-TR 16791 | CEN-TR 16791

## DE
| domain | dynamic building envelope
| code | service | 1
► | DE-1 | Window solar shading control |  | Service group: | Window control
| Functionality levels |  | IMPACTS
|  |  | Energy savings on site | Flexibility for the grid and storage | Comfort | Convenience | Wellbeing and health | maintenance & fault prediction | information to occupants
| level 0 | No sun shading or only manual operation | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 1 | Motorized operation with manual control | 1 | 0 | 1 | 1 | 0 | 0 | 0
| level 2 | Motorized operation with automatic control based on sensor data | 2 | 0 | 1 | 2 | 1 | 0 | 0
| level 3 | Combined light/blind/HVAC control | 3 | 0 | 2 | 3 | 2 | 0 | 0
| level 4 | Predictive blind control (e.g. based on weather forecast) | 3 | 0 | 3 | 3 | 3 | 0 | 0
Information sources
Standard?
| code | service | 1
► | DE-2 | Window open/closed control, combined with HVAC system |  | Service group: | Window control
| Functionality levels |  | IMPACTS
|  |  | Energy savings on site | Flexibility for the grid and storage | Comfort | Convenience | Wellbeing and health | maintenance & fault prediction | information to occupants
| level 0 | Manual operation or only fixed windows | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 1 | Open/closed detection to shut down heating or cooling systems | 2 | 0 | 1 | 1 | 0 | 0 | 0
| level 2 | Level 1 + Automised mechanical window opening based on room sensor data | 2 | 0 | 2 | 1 | 1 | 0 | 0
| level 3 | Level 2 + Centralized coordination of operable windows, e.g. to control free natural night cooling | 2 | 0 | 2 | 2 | 1 | 0 | 0
| level 4 | 0
Information sources
Standard?
| Functionality levels |  | IMPACTS
|  |  | Energy savings on site | Flexibility for the grid and storage | Comfort | Convenience | Wellbeing and health | maintenance & fault prediction | information to occupants
| level 0 | #REF! | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 1 | #REF! | + | 0 | 0 | ++ | 0 | 0 | 0
| level 2 | #REF! | +++ | 0 | 0 | +++ | 0 | 0 | 0
| level 3 | #REF! | - | - | - | - | - | - | -
| level 4 | #REF!
Information sources
Standard?
| code | service | 1
| DE-4 | Reporting information regarding performance of dynamic building envelope systems |  | Service group: | Feedback - Reporting information
| Functionality levels |  | IMPACTS
|  |  | Energy savings on site | Flexibility for the grid and storage | Comfort | Convenience | Wellbeing and health | maintenance & fault prediction | information to occupants
| level 0 | No reporting | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 1 | Position of each product & fault detection | 0 | 0 | 0 | 0 | 0 | 1 | 1
| level 2 | Position of each product, fault detection & predictive maintenance | 0 | 0 | 0 | 0 | 0 | 1 | 2
| level 3 | Position of each product, fault detection, predictive maintenance, real-time sensor data (wind, lux, temperature…) | 0 | 0 | 0 | 0 | 0 | 1 | 3
| level 4 | Position of each product, fault detection, predictive maintenance, real-time & historical sensor data (wind, lux, temperature…) | 0 | 0 | 0 | 1 | 0 | 2 | 3
Information sources
Standard?

## electricity
| domain | Electricity
| code | service | 1
► | electricity-2 | Reporting information regarding local electricity generation | Service group: |  | Feedback - Reporting information
| Functionality levels |  | IMPACTS
|  |  | Energy savings on site | Flexibility for the grid and storage | Comfort | Convenience | Wellbeing and health | maintenance & fault prediction | information to occupants
| level 0 | None | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 1 | Current generation data available | 1 | 0 | 0 | 0 | 0 | 1 | 1
| level 2 | Actual values and historical data | 1 | 0 | 0 | 0 | 0 | 1 | 2
| level 3 | Performance evaluation including forecasting and/or benchmarking | 1 | 0 | 0 | 0 | 0 | 1 | 3
| level 4 | Performance evaluation including forecasting and/or benchmarking; also including predictive management and fault detection | 1 | 0 | 0 | 1 | 0 | 2 | 3
|  | Information sources | IEC 61850-7-420 | IEC 61850-7-420
Standard?
| code | service | 1
► | electricity-3 | Storage of (locally generated) electricity | Service group: |  | DER - Storage
| Functionality levels |  | IMPACTS
|  |  | Energy savings on site | Flexibility for the grid and storage | Comfort | Convenience | Wellbeing and health | maintenance & fault prediction | information to occupants
| level 0 | None | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 1 | On site storage of electricity (e.g. electric battery) | 0 | 1 | 0 | 2 | 0 | 0 | 0
| level 2 | On site storage of energy (e.g. electric battery or thermal storage) with controller based on grid signals | 0 | 2 | 0 | 2 | 0 | 0 | 0
| level 3 | On site storage of energy (e.g. electric battery or thermal storage) with controller optimising the use of locally generated electricity | 0 | 2 | 0 | 2 | 0 | 0 | 0
| level 4 | On site storage of energy (e.g. electric battery or thermal storage) with controller optimising the use of locally generated electricity and possibility to feed back into the grid | 0 | 3 | 0 | 2 | 0 | 0 | 0
Information sources
Standard?
| code | service | 1
► | electricity-4 | Optimizing self-consumption of locally generated electricity | Service group: |  | DER- Optimization
| Functionality levels |  | IMPACTS
|  |  | Energy savings on site | Flexibility for the grid and storage | Comfort | Convenience | Wellbeing and health | maintenance & fault prediction | information to occupants
| level 0 | None | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 1 | Scheduling electricity consumption (plug loads, white goods, etc.) | 0 | 1 | 0 | 1 | 0 | 0 | 0
| level 2 | Automated management of local electricity consumption based on current renewable energy availability | 0 | 2 | 0 | 2 | 0 | 0 | 0
| level 3 | Automated management of local electricity consumption based on current and predicted energy needs and renewable energy availability | 0 | 3 | 0 | 2 | 0 | 0 | 0
| level 4 | 0
Information sources
Standard?
| code | service | 1
► | electricity-5 | Control of combined heat and power plant (CHP) | Service group: |  | DER - Generation Control
| Functionality levels |  | IMPACTS
|  |  | Energy savings on site | Flexibility for the grid and storage | Comfort | Convenience | Wellbeing and health | maintenance & fault prediction | information to occupants
| level 0 | CHP control based on scheduled runtime management and/or current heat energy demand | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 1 | CHP runtime control influenced by the fluctuating availability of RES; overproduction will be fed into the grid | 1 | 1 | 0 | 1 | 0 | 0 | 0
| level 2 | CHP runtime control influenced by the fluctuating availability of RES and grid signals; dynamic charging and runtime control to optimise self-consumption of renewables | 2 | 2 | 0 | 1 | 0 | 0 | 0
| level 3 | 0 | - | - | - | - | - | - | -
| level 4 | 0
Information sources
Standard?
| code | service | 1
| electricity-8 | Support of (micro)grid operation modes | Service group: |  | DSM- Storage
| Functionality levels |  | IMPACTS
|  |  | Energy savings on site | Flexibility for the grid and storage | Comfort | Convenience | Wellbeing and health | maintenance & fault prediction | information to occupants
| level 0 | None | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 1 | Automated management of (building-level) electricity consumption based on grid signals | 0 | 2 | 0 | 2 | 0 | 0 | 0
| level 2 | Automated management of (building-level) electricity consumption and electricity supply to neighbouring buildings (microgrid) or grid | 0 | 2 | 0 | 2 | 0 | 0 | 0
| level 3 | Automated management of (building-level) electricity consumption and supply, with potential to continue limited off-grid operation (island mode) | 0 | 3 | 0 | 3 | 0 | 0 | 0
| level 4 | 0
Information sources
|  | Standard? | IEC TC 57 | IEC TC 57 |  |  |  | IEC TC 57 | IEC TC 57
| Functionality levels |  | IMPACTS
|  |  | Energy savings on site | Flexibility for the grid and storage | Comfort | Convenience | Wellbeing and health | maintenance & fault prediction | information to occupants
| level 0 | #REF! | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 1 | #REF! | 0 | ++ | -- | -- | 0 | 0 | 0
| level 2 | #REF! | 0 | ++ | -- | -- | 0 | 0 | 0
| level 3 | #REF! | - | - | - | - | - | - | -
| level 4 | #REF!
Information sources
Standard?
| code | service | 1
| electricity-11 | Reporting information regarding energy storage | Service group: |  | Feedback - Reporting information
| Functionality levels |  | IMPACTS
|  |  | Energy savings on site | Flexibility for the grid and storage | Comfort | Convenience | Wellbeing and health | maintenance & fault prediction | information to occupants
| level 0 | None | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 1 | Current state of charge (SOC) data available | 1 | 0 | 0 | 0 | 0 | 1 | 1
| level 2 | Actual values and historical data | 1 | 0 | 0 | 0 | 0 | 1 | 2
| level 3 | Performance evaluation including forecasting and/or benchmarking | 1 | 0 | 0 | 0 | 0 | 1 | 3
| level 4 | Performance evaluation including forecasting and/or benchmarking; also including predictive management and fault detection | 1 | 0 | 0 | 1 | 0 | 2 | 3
Information sources
Standard?
| code | service | 1
| electricity-12 | Reporting information regarding electricity consumption | Service group: |  | Feedback - Reporting information
| Functionality levels |  | IMPACTS
|  |  | Energy savings on site | Flexibility for the grid and storage | Comfort | Convenience | Wellbeing and health | maintenance & fault prediction | information to occupants
| level 0 | None | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 1 | reporting on current electricity consumption on building level | 0 | 0 | 0 | 0 | 0 | 0 | 1
| level 2 | real-time feedback or benchmarking on building level | 1 | 0 | 0 | 0 | 0 | 0 | 2
| level 3 | real-time feedback or benchmarking on appliance level | 2 | 0 | 0 | 0 | 0 | 1 | 3
| level 4 | real-time feedback or benchmarking on appliance level with automated personalized recommendations | 3 | 0 | 0 | 1 | 0 | 2 | 3
Information sources
Standard?

## EV
| domain | Electric vehicle charging
| Functionality levels |  | IMPACTS
|  |  | Energy savings on site | Flexibility for the grid and storage | Comfort | Convenience | Wellbeing and health | maintenance & fault prediction | information to occupants
| level 0 | #REF! | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 1 | #REF! | + | +++ | 0 | + | 0 | + | 0
| level 2 | #REF! | - | - | - | - | - | - | -
| level 3 | #REF! | - | - | - | - | - | - | -
| level 4 | #REF!
Information sources
Standard?
| code | service | 1
► | EV-15 | EV Charging Capacity |  | Service group: | EV Charging
| Functionality levels |  | IMPACTS
|  |  | Energy savings on site | Flexibility for the grid and storage | Comfort | Convenience | Wellbeing and health | maintenance & fault prediction | information to occupants
| level 0 | not present | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 1 | ducting (or simple power plug) available | 0 | 0 | 0 | 1 | 0 | 0 | 0
| level 2 | 0-9% of parking spaces has recharging points | 0 | 0 | 0 | 2 | 0 | 0 | 0
| level 3 | 10-50% or parking spaces has recharging point | 0 | 0 | 0 | 3 | 0 | 0 | 0
| level 4 | >50% of parking spaces has recharging point | 0 | 0 | 0 | 3 | 0 | 0 | 0
| code | service | 1
► | EV-16 | EV Charging Grid balancing |  | Service group: | EV Charging - Grid
| Functionality levels |  | IMPACTS
|  |  | Energy savings on site | Flexibility for the grid and storage | Comfort | Convenience | Wellbeing and health | maintenance & fault prediction | information to occupants
| level 0 | Not present (uncontrolled charging) | 0 | -2 | 0 | 0 | 0 | 0 | 0
| level 1 | 1-way controlled charging (e.g. including desired departure time and grid signals for optimization) | 0 | 1 | 0 | 2 | 0 | 0 | 0
| level 2 | 2-way controlled charging (e.g. including desired departure time and grid signals for optimization) | 0 | 3 | 0 | 2 | 0 | 0 | 0
| level 3 | 0
| level 4 | 0
| code | service | 1
► | EV-17 | EV charging information and connectivity |  | Service group: | EV Charging - connectivity
| Functionality levels |  | IMPACTS
|  |  | Energy savings on site | Flexibility for the grid and storage | Comfort | Convenience | Wellbeing and health | maintenance & fault prediction | information to occupants
| level 0 | No information available | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 1 | Reporting information on EV charging status to occupant | 0 | 0 | 0 | 1 | 0 | 0 | 2
| level 2 | Reporting information on EV charging status to occupant AND automatic identification and authorizition of the driver to the charging station (ISO 15118 compliant) | 0 | 1 | 0 | 1 | 0 | 0 | 3
| level 3 | 0
| level 4 | 0

## MC
| domain | Monitoring and control
| Functionality levels |  | IMPACTS
|  |  | Energy savings on site | Flexibility for the grid and storage | Comfort | Convenience | Wellbeing and health | maintenance & fault prediction | information to occupants
| level 0 | #REF! | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 1 | #REF! | + | 0 | + | 0 | 0 | 0 | 0
| level 2 | #REF! | ++ | 0 | + | 0 | 0 | 0 | 0
| level 3 | #REF! | - | - | - | - | - | - | -
| level 4 | #REF!
Information sources
Standard?
| code | service | 1
► | MC-3 | Run time management of HVAC systems |  | Service group: | HVAC interaction control
| Functionality levels |  | IMPACTS
|  |  | Energy savings on site | Flexibility for the grid and storage | Comfort | Convenience | Wellbeing and health | maintenance & fault prediction | information to occupants
| level 0 | Manual setting | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 1 | Runtime setting of heating and cooling plants following a predefined time schedule | 1 | 1 | 1 | 1 | 0 | 0 | 0
| level 2 | Heating and cooling plant on/off control based on building loads | 2 | 1 | 2 | 2 | 1 | 0 | 0
| level 3 | Heating and cooling plant on/off control based on predictive control or grid signals | 3 | 2 | 2 | 3 | 1 | 0 | 0
| level 4 | 0
Information sources
Standard?
| code | service | 1
► | MC-4 | Detecting faults of technical building systems and providing support to the diagnosis of these faults |  | Service group: | Fault detection
| Functionality levels |  | IMPACTS
|  |  | Energy savings on site | Flexibility for the grid and storage | Comfort | Convenience | Wellbeing and health | maintenance & fault prediction | information to occupants
| level 0 | No central indication of detected faults and alarms | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 1 | With central indication of detected faults and alarms for at least 2 relevant TBS | 0 | 0 | 0 | 1 | 1 | 1 | 1
| level 2 | With central indication of detected faults and alarms for all relevant TBS | 0 | 0 | 0 | 2 | 2 | 2 | 2
| level 3 | With central indication of detected faults and alarms for all relevant TBS, including diagnosing functions | 0 | 0 | 0 | 3 | 3 | 3 | 3
| level 4 | 0
Information sources
Standard?
| Functionality levels |  | IMPACTS
|  |  | Energy savings on site | Flexibility for the grid and storage | Comfort | Convenience | Wellbeing and health | maintenance & fault prediction | information to occupants
| level 0 | #REF! | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 1 | #REF! | 0 | 0 | 0 | 0 | 0 | 0 | +
| level 2 | #REF! | + | 0 | 0 | 0 | 0 | 0 | ++
| level 3 | #REF! | + | 0 | 0 | 0 | 0 | 0 | +++
| level 4 | #REF!
Information sources
Standard?
| code | service | 1
► | MC-9 | Occupancy detection: connected services |  | Service group: | TBS interaction control
| Functionality levels |  | IMPACTS
|  |  | Energy savings on site | Flexibility for the grid and storage | Comfort | Convenience | Wellbeing and health | maintenance & fault prediction | information to occupants
| level 0 | None | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 1 | Occupancy detection for individual functions, e.g. lighting | 1 | 0 | 1 | 1 | 0 | 1 | 0
| level 2 | Centralised occupant detection which feeds in to several TBS such as lighting and heating | 1 | 0 | 1 | 1 | 0 | 2 | 0
| level 3 | 0 | - | - | - | - | - | - | -
| level 4 | 0
Information sources
Standard?
| Functionality levels |  | IMPACTS
|  |  | Energy savings on site | Flexibility for the grid and storage | Comfort | Convenience | Wellbeing and health | maintenance & fault prediction | information to occupants
| level 0 | #REF! | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 1 | #REF! | + | + | 0 | + | 0 | + | 0
| level 2 | #REF! | ++ | + | 0 | ++ | 0 | ++ | +
| level 3 | #REF! | ++ | +++ | 0 | ++ | 0 | ++ | +
| level 4 | #REF!
Information sources
Standard?
| code | service | 1
► | MC-13 | Central reporting of TBS performance and energy use |  | Service group: | Feedback - Reporting information
| Functionality levels |  | IMPACTS
|  |  | Energy savings on site | Flexibility for the grid and storage | Comfort | Convenience | Wellbeing and health | maintenance & fault prediction | information to occupants
| level 0 | None | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 1 | Central or remote reporting of realtime energy use per energy carrier | 1 | 0 | 0 | 1 | 0 | 1 | 1
| level 2 | Central or remote reporting of realtime energy use per energy carrier, combining TBS of at least 2 domains in one interface | 1 | 0 | 0 | 2 | 0 | 2 | 2
| level 3 | Central or remote reporting of realtime energy use per energy carrier, combining TBS of all main domains in one interface | 1 | 0 | 0 | 3 | 0 | 3 | 3
| level 4 | 0
Information sources
Standard?
| Functionality levels |  | IMPACTS
|  |  | Energy savings on site | Flexibility for the grid and storage | Comfort | Convenience | Wellbeing and health | maintenance & fault prediction | information to occupants
| level 0 | #REF! | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 1 | #REF! | + | ++ | 0 | 0 | 0 | - | 0
| level 2 | #REF! | + | ++ | 0 | 0 | 0 | - | 0
| level 3 | #REF! | - | - | - | - | - | - | -
| level 4 | #REF!
Information sources
Standard?
| code | service | 1
| MC-25 | Smart Grid Integration |  | Service group: | Smart Grid Integration
| Functionality levels |  | IMPACTS
|  |  | Energy savings on site | Flexibility for the grid and storage | Comfort | Convenience | Wellbeing and health | maintenance & fault prediction | information to occupants
| level 0 | None - No harmonization between grid and TBS; building is operated independently from the grid load | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 1 | Demand side management possible for (some) individual TBS, but not coordinated over various domains | 0 | 2 | 0 | 0 | 0 | 0 | 0
| level 2 | Coordinated demand side management of multiple TBS | 1 | 3 | 0 | 1 | 0 | 0 | 0
| level 3 | 0
| level 4 | 0
Information sources
Standard?
| Functionality levels |  | IMPACTS
|  |  | Energy savings on site | Flexibility for the grid and storage | Comfort | Convenience | Wellbeing and health | maintenance & fault prediction | information to occupants
| level 0 | #REF! | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 1 | #REF! | 0 | + | 0 | 0 | 0 | 0 | 0
| level 2 | #REF! | 0 | ++ | 0 | 0 | 0 | 0 | 0
| level 3 | #REF! | 0 | +++ | 0 | 0 | 0 | 0 | 0
| level 4 | #REF!
Information sources
Standard?
| code | service | 1
| MC-28 | Reporting information regarding demand side management performance and operation |  | Service group: | Feedback - Reporting information
| Functionality levels |  | IMPACTS
|  |  | Energy savings on site | Flexibility for the grid and storage | Comfort | Convenience | Wellbeing and health | maintenance & fault prediction | information to occupants
| level 0 | None | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 1 | Reporting information on current DSM status, including managed energy flows | 0 | 1 | 0 | 0 | 0 | 0 | 2
| level 2 | Reporting information on currenthistorical and predicted DSM status, including managed energy flows | 0 | 2 | 0 | 0 | 0 | 1 | 3
| level 3 | 0
| level 4 | 0
Information sources
Standard?
| code | service | 1
| MC-29 | Override of DSM control |  | Service group: | Override control
| Functionality levels |  | IMPACTS
|  |  | Energy savings on site | Flexibility for the grid and storage | Comfort | Convenience | Wellbeing and health | maintenance & fault prediction | information to occupants
| level 0 | No DSM control | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 1 | DSM control without the possibility to override this control by the building user (occupant or facility manager) | 0 | 3 | -2 | 0 | 0 | -1 | -2
| level 2 | Manual override and reactivation of DSM control by the building user | 0 | 1 | 0 | 1 | 0 | 0 | 0
| level 3 | Scheduled override of DSM control (and reactivation) by the building user | 0 | 1 | 0 | 2 | 0 | 1 | 0
| level 4 | Scheduled override of DSM control and reactivation with optimised control | 0 | 2 | 0 | 3 | 0 | 1 | 0
Information sources
Standard?
| code | service | 1
| MC-30 | Single platform that allows automated control & coordination between TBS + optimization of energy flow based on occupancy, weather and grid signals |  | Service group: | Single platform that allows automated control & coordination between TBS + optimization of energy flow based on occupancy, weather and grid signals
| Functionality levels |  | IMPACTS
|  |  | Energy savings on site | Flexibility for the grid and storage | Comfort | Convenience | Wellbeing and health | maintenance & fault prediction | information to occupants
| level 0 | None | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 1 | Single platform that allows manual control of multiple TBS | 0 | 0 | 0 | 1 | 0 | 1 | 0
| level 2 | Single platform that allows automated control & coordination between TBS | 1 | 0 | 0 | 2 | 0 | 1 | 0
| level 3 | Single platform that allows automated control & coordination between TBS + optimization of energy flow based on occupancy, weather and grid signals | 2 | 0 | 0 | 3 | 0 | 1 | 0
| level 4 | 0
Information sources
Standard?

## Weightings
DEFAULT WEIGHTING FACTORS METHOD B
residential
DOMAIN WEIGHTINGS
northern europe | [8 empty] | western europe | [8 empty] | southern europe | [8 empty] | north-eastern europe | [8 empty] | south-eastern europe
| Energy savings on site | Flexibility for the grid and storage | Comfort | Convenience | Health & Wellbeing | Maintenance & fault prediction | Information to occupants |  |  | Energy savings on site | Flexibility for the grid and storage | Comfort | Convenience | Health & Wellbeing | Maintenance & fault prediction | Information to occupants |  |  | Energy savings on site | Flexibility for the grid and storage | Comfort | Convenience | Health & Wellbeing | Maintenance & fault prediction | Information to occupants |  |  | Energy savings on site | Flexibility for the grid and storage | Comfort | Convenience | Health & Wellbeing | maintenance & fault prediction | information to occupants |  |  | Energy savings on site | Flexibility for the grid and storage | Comfort | Convenience | Health & Wellbeing | Maintenance & fault prediction | Information to occupants
Heating system | 0.29909 | 0.42673 | 0.16 | 0.1 | 0.2 | 0.3146 | 0.11429 |  | Heating system | 0.33967 | 0.45722 | 0.16 | 0.1 | 0.2 | 0.34643 | 0.11429 |  | Heating system | 0.31666 | 0.37624 | 0.16 | 0.1 | 0.2 | 0.3284 | 0.11429 |  | Heating system | 0.30383 | 0.41172 | 0.16 | 0.1 | 0.2 | 0.30636 | 0.11429 |  | Heating system | 0.20621 | 0.24438 | 0.16 | 0.1 | 0.2 | 0.20871 | 0.11429
Domestic Hot Water | 0.092805 | 0.13241 | 0 | 0.1 | 0 | 0.097617 | 0.11429 |  | Domestic Hot Water | 0.07621 | 0.10258 | 0 | 0.1 | 0 | 0.077729 | 0.11429 |  | Domestic Hot Water | 0.099794 | 0.11857 | 0 | 0.1 | 0 | 0.10349 | 0.11429 |  | Domestic Hot Water | 0.13928 | 0.18873 | 0 | 0.1 | 0 | 0.14044 | 0.11429 |  | Domestic Hot Water | 0.058032 | 0.068776 | 0 | 0.1 | 0 | 0.058737 | 0.11429
Cooling system | 0 | 0 | 0.16 | 0.1 | 0.2 | 0 | 0.11429 |  | Cooling system | 0.030389 | 0.040906 | 0.16 | 0.1 | 0.2 | 0.030995 | 0.11429 |  | Cooling system | 0.068809 | 0.081755 | 0.16 | 0.1 | 0.2 | 0.07136 | 0.11429 |  | Cooling system | 0 | 0 | 0.16 | 0.1 | 0.2 | 0 | 0.11429 |  | Cooling system | 0.14659 | 0.17373 | 0.16 | 0.1 | 0.2 | 0.14837 | 0.11429
Controlled ventilation | 0.18736 | 0 | 0.16 | 0.1 | 0.2 | 0.19708 | 0.11429 |  | Controlled ventilation | 0.17817 | 0 | 0.16 | 0.1 | 0.2 | 0.18172 | 0.11429 |  | Controlled ventilation | 0.091952 | 0 | 0.16 | 0.1 | 0.2 | 0.095361 | 0.11429 |  | Controlled ventilation | 0.19033 | 0 | 0.16 | 0.1 | 0.2 | 0.19192 | 0.11429 |  | Controlled ventilation | 0.10816 | 0 | 0.16 | 0.1 | 0.2 | 0.10948 | 0.11429
Lighting | 0.036968 | 0 | 0.16 | 0.1 | 0 | 0 | 0 |  | Lighting | 0.014649 | 0 | 0.16 | 0.1 | 0 | 0 | 0 |  | Lighting | 0.026813 | 0 | 0.16 | 0.1 | 0 | 0 | 0 |  | Lighting | 0.0062019 | 0 | 0.16 | 0.1 | 0 | 0 | 0 |  | Lighting | 0.0089994 | 0 | 0.16 | 0.1 | 0 | 0 | 0
Electricity: renewables & storage | 0.13377 | 0.19086 | 0 | 0.1 | 0 | 0.14071 | 0.11429 |  | Electricity: renewables & storage | 0.11091 | 0.14929 | 0 | 0.1 | 0 | 0.11312 | 0.11429 |  | Electricity: renewables & storage | 0.14597 | 0.17343 | 0 | 0.1 | 0 | 0.15138 | 0.11429 |  | Electricity: renewables & storage | 0.11036 | 0.14955 | 0 | 0.1 | 0 | 0.11128 | 0.11429 |  | Electricity: renewables & storage | 0.22201 | 0.26311 | 0 | 0.1 | 0 | 0.2247 | 0.11429
Dynamic Envelope | 0.05 | 0 | 0.16 | 0.1 | 0.2 | 0.05 | 0.11429 |  | Dynamic Envelope | 0.05 | 0 | 0.16 | 0.1 | 0.2 | 0.05 | 0.11429 |  | Dynamic Envelope | 0.05 | 0 | 0.16 | 0.1 | 0.2 | 0.05 | 0.11429 |  | Dynamic Envelope | 0.05 | 0 | 0.16 | 0.1 | 0.2 | 0.05 | 0.11429 |  | Dynamic Envelope | 0.05 | 0 | 0.16 | 0.1 | 0.2 | 0.05 | 0.11429
Electric Vehicle Charging | 0 | 0.05 | 0 | 0.1 | 0 | 0 | 0.11429 |  | Electric Vehicle Charging | 0 | 0.05 | 0 | 0.1 | 0 | 0 | 0.11429 |  | Electric Vehicle Charging | 0 | 0.05 | 0 | 0.1 | 0 | 0 | 0.11429 |  | Electric Vehicle Charging | 0 | 0.05 | 0 | 0.1 | 0 | 0 | 0.11429 |  | Electric Vehicle Charging | 0 | 0.05 | 0 | 0.1 | 0 | 0 | 0.11429
Monitoring & Control | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 |  | Monitoring & Control | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 |  | Monitoring & Control | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 |  | Monitoring & Control | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 |  | Monitoring & Control | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
| 1 | 1 | 1 | 1 | 1 | 1 | 1 |  |  | 1 | 1 | 1 | 1 | 1 | 1 | 1 |  |  | 1 | 1 | 1 | 1 | 1 | 1 | 1 |  |  | 1 | 1 | 1 | 1 | 1 | 1 | 1 |  |  | 1 | 1 | 1 | 1 | 1 | 1 | 1
IMPACT WEIGHTINGS | [8 empty] | IMPACT WEIGHTINGS | [8 empty] | IMPACT WEIGHTINGS | [8 empty] | IMPACT WEIGHTINGS | [8 empty] | IMPACT WEIGHTINGS
| Energy savings on site | Flexibility for the grid and storage | Comfort | Convenience | Health & Wellbeing | Maintenance & fault prediction | Information to occupants |  |  | Energy savings on site | Flexibility for the grid and storage | Comfort | Convenience | Health & Wellbeing | Maintenance & fault prediction | Information to occupants |  |  | Energy savings on site | Flexibility for the grid and storage | Comfort | Convenience | Health & Wellbeing | Maintenance & fault prediction | Information to occupants |  |  | Energy savings on site | Flexibility for the grid and storage | Comfort | Convenience | Wellbeing and health | maintenance & fault prediction | information to occupants |  |  | Energy savings on site | Flexibility for the grid and storage | Comfort | Convenience | Health & Wellbeing | Maintenance & fault prediction | Information to occupants
| 0.16667 | 0.33333 | 0.083333 | 0.083333 | 0.083333 | 0.16667 | 0.083333 | 1 |  | 0.16667 | 0.33333 | 0.083333 | 0.083333 | 0.083333 | 0.16667 | 0.083333 | 1 |  | 0.16667 | 0.33333 | 0.083333 | 0.083333 | 0.083333 | 0.16667 | 0.083333 | 1 |  | 0.16667 | 0.33333 | 0.083333 | 0.083333 | 0.083333 | 0.16667 | 0.083333 | 1 |  | 0.16667 | 0.33333 | 0.083333 | 0.083333 | 0.083333 | 0.16667 | 0.083333 | 1
non-residential
DOMAIN WEIGHTINGS
northern europe | [8 empty] | western europe | [8 empty] | southern europe | [8 empty] | north-eastern europe | [8 empty] | south-eastern europe
| Energy savings on site | Flexibility for the grid and storage | Comfort | Convenience | Health & Wellbeing | Maintenance & fault prediction | Information to occupants |  |  | Energy savings on site | Flexibility for the grid and storage | Comfort | Convenience | Health & Wellbeing | Maintenance & fault prediction | Information to occupants |  |  | Energy savings on site | Flexibility for the grid and storage | Comfort | Convenience | Health & Wellbeing | Maintenance & fault prediction | Information to occupants |  |  | Energy savings on site | Flexibility for the grid and storage | Comfort | Convenience | Health & Wellbeing | maintenance & fault prediction | information to occupants |  |  | Energy savings on site | Flexibility for the grid and storage | Comfort | Convenience | Health & Wellbeing | Maintenance & fault prediction | Information to occupants
Heating system | 0.31322 | 0.49384 | 0.16 | 0.1 | 0.2 | 0.34962 | 0.11429 |  | Heating system | 0.27278 | 0.40662 | 0.16 | 0.1 | 0.2 | 0.31659 | 0.11429 |  | Heating system | 0.30198 | 0.41746 | 0.16 | 0.1 | 0.2 | 0.35938 | 0.11429 |  | Heating system | 0.29248 | 0.44428 | 0.16 | 0.1 | 0.2 | 0.32403 | 0.11429 |  | Heating system | 0.28706 | 0.42184 | 0.16 | 0.1 | 0.2 | 0.32574 | 0.11429
Domestic Hot Water | 0.053686 | 0.084645 | 0 | 0.1 | 0 | 0.059926 | 0.11429 |  | Domestic Hot Water | 0.082585 | 0.12311 | 0 | 0.1 | 0 | 0.095848 | 0.11429 |  | Domestic Hot Water | 0.10727 | 0.1483 | 0 | 0.1 | 0 | 0.12766 | 0.11429 |  | Domestic Hot Water | 0.093878 | 0.1426 | 0 | 0.1 | 0 | 0.10401 | 0.11429 |  | Domestic Hot Water | 0.11572 | 0.17006 | 0 | 0.1 | 0 | 0.13131 | 0.11429
Cooling system | 0.093696 | 0.14773 | 0.16 | 0.1 | 0.2 | 0.10459 | 0.11429 |  | Cooling system | 0.1267 | 0.18887 | 0.16 | 0.1 | 0.2 | 0.14705 | 0.11429 |  | Cooling system | 0.11743 | 0.16234 | 0.16 | 0.1 | 0.2 | 0.13975 | 0.11429 |  | Cooling system | 0.083878 | 0.12741 | 0.16 | 0.1 | 0.2 | 0.092927 | 0.11429 |  | Cooling system | 0.074586 | 0.1096 | 0.16 | 0.1 | 0.2 | 0.084635 | 0.11429
Controlled ventilation | 0.19621 | 0 | 0.16 | 0.1 | 0.2 | 0.21902 | 0.11429 |  | Controlled ventilation | 0.14309 | 0 | 0.16 | 0.1 | 0.2 | 0.16607 | 0.11429 |  | Controlled ventilation | 0.087687 | 0 | 0.16 | 0.1 | 0.2 | 0.10435 | 0.11429 |  | Controlled ventilation | 0.18322 | 0 | 0.16 | 0.1 | 0.2 | 0.20299 | 0.11429 |  | Controlled ventilation | 0.15058 | 0 | 0.16 | 0.1 | 0.2 | 0.17087 | 0.11429
Lighting | 0.078094 | 0 | 0.16 | 0.1 | 0 | 0 | 0 |  | Lighting | 0.10378 | 0 | 0.16 | 0.1 | 0 | 0 | 0 |  | Lighting | 0.11979 | 0 | 0.16 | 0.1 | 0 | 0 | 0 |  | Lighting | 0.073036 | 0 | 0.16 | 0.1 | 0 | 0 | 0 |  | Lighting | 0.089049 | 0 | 0.16 | 0.1 | 0 | 0 | 0
Electricity: renewables & storage | 0.01509 | 0.023792 | 0 | 0.1 | 0 | 0.016844 | 0.11429 |  | Electricity: renewables & storage | 0.021067 | 0.031404 | 0 | 0.1 | 0 | 0.02445 | 0.11429 |  | Electricity: renewables & storage | 0.015845 | 0.021904 | 0 | 0.1 | 0 | 0.018856 | 0.11429 |  | Electricity: renewables & storage | 0.023509 | 0.03571 | 0 | 0.1 | 0 | 0.026045 | 0.11429 |  | Electricity: renewables & storage | 0.033001 | 0.048496 | 0 | 0.1 | 0 | 0.037447 | 0.11429
Dynamic Envelope | 0.05 | 0 | 0.16 | 0.1 | 0.2 | 0.05 | 0.11429 |  | Dynamic Envelope | 0.05 | 0 | 0.16 | 0.1 | 0.2 | 0.05 | 0.11429 |  | Dynamic Envelope | 0.05 | 0 | 0.16 | 0.1 | 0.2 | 0.05 | 0.11429 |  | Dynamic Envelope | 0.05 | 0 | 0.16 | 0.1 | 0.2 | 0.05 | 0.11429 |  | Dynamic Envelope | 0.05 | 0 | 0.16 | 0.1 | 0.2 | 0.05 | 0.11429
Electric Vehicle Charging | 0 | 0.05 | 0 | 0.1 | 0 | 0 | 0.11429 |  | Electric Vehicle Charging | 0 | 0.05 | 0 | 0.1 | 0 | 0 | 0.11429 |  | Electric Vehicle Charging | 0 | 0.05 | 0 | 0.1 | 0 | 0 | 0.11429 |  | Electric Vehicle Charging | 0 | 0.05 | 0 | 0.1 | 0 | 0 | 0.11429 |  | Electric Vehicle Charging | 0 | 0.05 | 0 | 0.1 | 0 | 0 | 0.11429
Monitoring & Control | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 |  | Monitoring & Control | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 |  | Monitoring & Control | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 |  | Monitoring & Control | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 |  | Monitoring & Control | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
| 1 | 1 | 1 | 1 | 1 | 1 | 1 |  |  | 1 | 1 | 1 | 1 | 1 | 1 | 1 |  |  | 1 | 1 | 1 | 1 | 1 | 1 | 1 |  |  | 1 | 1 | 1 | 1 | 1 | 1 | 1 |  |  | 1 | 1 | 1 | 1 | 1 | 1 | 1
IMPACT WEIGHTINGS | [8 empty] | IMPACT WEIGHTINGS | [8 empty] | IMPACT WEIGHTINGS | [8 empty] | IMPACT WEIGHTINGS | [8 empty] | IMPACT WEIGHTINGS
| Energy savings on site | Flexibility for the grid and storage | Comfort | Convenience | Health & Wellbeing | Maintenance & fault prediction | Information to occupants |  |  | Energy savings on site | Flexibility for the grid and storage | Comfort | Convenience | Health & Wellbeing | Maintenance & fault prediction | Information to occupants |  |  | Energy savings on site | Flexibility for the grid and storage | Comfort | Convenience | Health & Wellbeing | Maintenance & fault prediction | Information to occupants |  |  | Energy savings on site | Flexibility for the grid and storage | Comfort | Convenience | Wellbeing and health | maintenance & fault prediction | information to occupants |  |  | Energy savings on site | Flexibility for the grid and storage | Comfort | Convenience | Health & Wellbeing | Maintenance & fault prediction | Information to occupants
| 0.16667 | 0.33333 | 0.083333 | 0.083333 | 0.083333 | 0.16667 | 0.083333 | 1 |  | 0.16667 | 0.33333 | 0.083333 | 0.083333 | 0.083333 | 0.16667 | 0.083333 | 1 |  | 0.16667 | 0.33333 | 0.083333 | 0.083333 | 0.083333 | 0.16667 | 0.083333 | 1 |  | 0.16667 | 0.33333 | 0.083333 | 0.083333 | 0.083333 | 0.16667 | 0.083333 | 1 |  | 0.16667 | 0.33333 | 0.083333 | 0.083333 | 0.083333 | 0.16667 | 0.083333 | 1
RELEVANCE OF DOMAIN TO IMPACT CRITERION
LEGEND
0 | the services within this domain have no contribution to the given impact criterion
1 | at least one service within this domain contributes to the given impact criterion
| Energy savings on site | Flexibility for the grid and storage | Comfort | Convenience | Wellbeing and health | maintenance & fault prediction | information to occupants
Heating system | 1 | 1 | 1 | 1 | 1 | 1 | 1
Domestic Hot Water | 1 | 1 | 0 | 1 | 0 | 1 | 1
Cooling system | 1 | 1 | 1 | 1 | 1 | 1 | 1
Controlled ventilation | 1 | 0 | 1 | 1 | 1 | 1 | 1
Lighting | 1 | 0 | 1 | 1 | 0 | 0 | 0
Electricity: renewables & storage | 1 | 1 | 0 | 1 | 0 | 1 | 1
Dynamic Envelope | 1 | 0 | 1 | 1 | 1 | 1 | 1
Electric Vehicle Charging | 0 | 1 | 0 | 1 | 0 | 0 | 1
Monitoring & Control | 1 | 1 | 0 | 1 | 0 | 1 | 1
ENERGY BALANCE DATA
RESIDENTIAL | WEIGHTINGS | North | West | South | North-East | South-East
| Heating | 39.8787 | 45.2891 | 42.2219 | 40.5106 | 27.4941
| DHW | 12.374 | 10.1614 | 13.3059 | 18.5702 | 7.7376
| Cooling | 0 | 4.0519 | 9.1745 | 0 | 19.5457
| Ventilation | 24.9819 | 23.7563 | 12.2602 | 25.3777 | 14.4219
| Lighting | 4.929 | 1.9532 | 3.575 | 0.82692 | 1.1999
| Electricity | 17.8363 | 14.7881 | 19.4624 | 14.7145 | 29.6008
|  | 3 | 4 | 5 | 6 | 7
NON RESIDENTIAL | WEIGHTINGS | North | West | South | North-East | South-East
| Heating | 41.7625 | 36.3708 | 40.2637 | 38.9971 | 38.2751
| DHW | 7.1582 | 11.0113 | 14.3029 | 12.5171 | 15.4297
| Cooling | 12.4928 | 16.8935 | 15.6576 | 11.1837 | 9.9448
| Ventilation | 26.162 | 19.0782 | 11.6916 | 24.4296 | 20.0771
| Lighting | 10.4125 | 13.8372 | 15.9716 | 9.7381 | 11.8732
| Electricity | 2.012 | 2.8089 | 2.1126 | 3.1345 | 4.4002

## Climate zones
Country | Climate zone
Iceland | North Europe
Norway | North Europe
Sweden | North Europe
Denmark | North Europe
Finland | North Europe
Czech Republic | North-East Europe
Estonia | North-East Europe
Latvia | North-East Europe
Lithuania | North-East Europe
Poland | North-East Europe
Slovakia | North-East Europe
Cyprus | South Europe
Greece | South Europe
Italy | South Europe
Malta | South Europe
Portugal | South Europe
Spain | South Europe
Bulgaria | South-East Europe
Croatia | South-East Europe
Hungary | South-East Europe
Romania | South-East Europe
Slovenia | South-East Europe
Austria | West Europe
Belgium | West Europe
France | West Europe
Germany | West Europe
Ireland | West Europe
Liechtenstein | West Europe
Luxembourg | West Europe
Netherlands | West Europe
Switzerland | West Europe
United Kingdom | West Europe